## ВВОД
Наименование станции | Насос | Артикул | Размеры |  | Q | H | P2 | NPSH | КПД
Hydro-FS-A 1/1 CRV 10-1 G2-B-80-16 | CRV 10-1C | 75211384 | В | 1650 | 0 | 13.75 | 0.102 | 0.427 | 0
|  |  | В1 | 613 | 5 | 11.45 | 0.242 | 0.948 | 54
Max расход: |  |  | В2 | 180 | 7 | 10.4 | 0.2843 | 1.241 | 63.51
Max напор: |  |  | Ш1 | 565 | 8 | 9.85 | 0.2993 | 1.449 | 66.12
Номинальный напор: |  |  | Ш2 | 520 | 9 | 9.25 | 0.3105 | 1.709 | 68.06
Количество насосов: |  |  | Ш3 | 1549 | 10 | 8.65 | 0.3178 | 2.067 | 69.23
Количество резервных насосов: |  |  | Шобщ | 1085 | 11 | 8 | 0.3208 | 2.553 | 69.5
Тип установки уплотнения: |  |  | Р1 | 1760 | 12 | 7.35 | 0.3192 | 3.094 | 68.65
|  |  | Р2 | 427 | 13 | 6.5995 | 0.3124 | 3.68 | 66.3
Корпус: |  |  | Р3 |  | 14 | 5.82 | 0.2996 | 4.326 | 61.81
Рабочее колесо: |  |  | Р4
Уплотнение вала: |  |  | РП | 385
Коллектор: |  |  | РВ | 100
ПАЗ
Температура окружающей среды: |  |  | ОТВ-Е | 12 отв. ø16
Относительная влажность воздуха: |  |  | ВШ | 1000
Max рабочее давление: |  |  | ШШ | 800
Стандарт трубного присоединения: |  |  | ШО | 860
Размер всасывающего патрубка: |  |  | К | 450
Размер напорного патрубка: |  |  | DN | 80
Допустимое давление фланцев:
Диапазон температуры жидкости:
Мощность (P2) одного насоса:
Номинальное напряжение:
Max потребление тока:
Схема пуска:
Степень защиты (IEC 34-5):
Температура хранения:
Масса (нетто):
Масса (брутто):

## HFS_CRV
Наименование | Насос | В | В1 | В2 | Ш1 | Ш2 | Ш3 | Шобщ | Р1 | Р2 | Р3 | Р4 | РП | РВ | ПАЗ | ОТВ-Е | ВШ | ШШ | ШО | К | DN | Общее кол-во | Основа | Резерв | Мощность | Ток | Схема пуска | Торцевое | Масса нетто | Артикул
Hydro-FS-A 1/1 CRV 10-1 G2-B-80-16 | CRV 10-1C | 1650 | 613 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 0.37 | 17.6 | прямой пуск (DOL) | HQQE | 239 | 75211384
Hydro-FS-A 1/1 CRV 10-2 G2-B-80-16 | CRV 10-2C | 1650 | 643 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 0.75 | 19 | прямой пуск (DOL) | HQQE | 243 | 75211387
Hydro-FS-A 1/1 CRV 10-3 G2-B-80-16 | CRV 10-3C | 1650 | 710 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 1.1 | 20.2 | прямой пуск (DOL) | HQQE | 251 | 75211388
Hydro-FS-A 1/1 CRV 10-4 G2-B-80-16 | CRV 10-4C | 1650 | 740 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 1.5 | 21.6 | прямой пуск (DOL) | HQQE | 267 | 75211385
Hydro-FS-A 1/1 CRV 10-5 G2-B-80-16 | CRV 10-5C | 1650 | 822 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 2.2 | 23.9 | прямой пуск (DOL) | HQQE | 269 | 75211371
Hydro-FS-A 1/1 CRV 10-6 G2-B-80-16 | CRV 10-6C | 1650 | 852 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 2.2 | 23.9 | прямой пуск (DOL) | HQQE | 271 | 75211389
Hydro-FS-A 1/1 CRV 10-9 G2-B-80-16 | CRV 10-9C | 1650 | 962 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 3 | 26.4 | прямой пуск (DOL) | HQQE | 287 | 75211376
Hydro-FS-A 1/1 CRV 10-12 G2-B-80-16 | CRV 10-12C | 1650 | 1085 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 4 | 23.8 | прямой пуск (DOL) | HQQE | 315 | 75211390
Hydro-FS-A 1/1 CRV 10-14 G2-B-80-16 | CRV 10-14C | 1650 | 1226 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 359 | 75211391
Hydro-FS-A 1/1 CRV 10-16 G2-B-80-25 | CRV 10-16C | 1650 | 1286 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 363 | При заказе
Hydro-FS-A 1/1 CRV 10-18 G2-B-80-25 | CRV 10-18C | 1650 | 1384 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 373 | При заказе
Hydro-FS-A 1/1 CRV 10-20 G2-B-80-25 | CRV 10-20C | 1650 | 1444 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 377 | При заказе
Hydro-FS-A 1/1 CRV 10-22 G2-B-80-25 | CRV 10-22C | 1650 | 1504 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 383 | При заказе
Hydro-FS-A 1/1 CRV 15-1 G2-B-80-16 | CRV 15-1C | 1650 | 672 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 1.1 | 20.2 | прямой пуск (DOL) | HQQE | 267 | 75211375
Hydro-FS-A 1/1 CRV 15-2 G2-B-80-16 | CRV 15-2C | 1650 | 769 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 2.2 | 23.9 | прямой пуск (DOL) | HQQE | 283 | 75211392
Hydro-FS-A 1/1 CRV 15-3 G2-B-80-16 | CRV 15-3C | 1650 | 834 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 3 | 26.4 | прямой пуск (DOL) | HQQE | 293 | 75211393
Hydro-FS-A 1/1 CRV 15-4 G2-B-80-16 | CRV 15-4C | 1650 | 912 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 4 | 23.8 | прямой пуск (DOL) | HQQE | 319 | 75211394
Hydro-FS-A 1/1 CRV 15-5 G2-B-80-16 | CRV 15-5C | 1650 | 957 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 4 | 23.8 | прямой пуск (DOL) | HQQE | 321 | 75211395
Hydro-FS-A 1/1 CRV 15-6 G2-B-80-16 | CRV 15-6C | 1650 | 1083 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 365 | 75211396
Hydro-FS-A 1/1 CRV 15-7 G2-B-80-16 | CRV 15-7C | 1650 | 1128 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 369 | 75211397
Hydro-FS-A 1/1 CRV 15-8 G2-B-80-16 | CRV 15-8C | 1650 | 1211 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 377 | 75211398
Hydro-FS-A 1/1 CRV 15-9 G2-B-80-16 | CRV 15-9C | 1650 | 1256 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 379 | 75211399
Hydro-FS-A 1/1 CRV 15-10 G2-B-80-16 | CRV 15-10C | 1650 | 1417 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 465 | 75211400
Hydro-FS-A 1/1 CRV 15-12 G2-B-80-25 | CRV 15-12C | 1650 | 1507 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 473 | При заказе
Hydro-FS-A 1/1 CRV 15-14 G2-B-80-25 | CRV 15-14C | 1650 | 1597 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 479 | При заказе
Hydro-FS-A 1/1 CRV 15-17 G2-B-80-25 | CRV 15-17C | 1650 | 1773 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 15 | 43.9 | звезда-треугольник (SD) | HQQE | 499 | При заказе
Hydro-FS-A 1/1 CRV 20-1 G2-B-80-16 | CRV 20-1C | 1650 | 672 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 1.1 | 20.2 | прямой пуск (DOL) | HQQE | 249 | 75211373
Hydro-FS-A 1/1 CRV 20-2 G2-B-80-16 | CRV 20-2C | 1650 | 769 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 2.2 | 23.9 | прямой пуск (DOL) | HQQE | 271 | 75211401
Hydro-FS-A 1/1 CRV 20-3 G2-B-80-16 | CRV 20-3C | 1650 | 867 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 4 | 23.8 | прямой пуск (DOL) | HQQE | 299 | 75211374
Hydro-FS-A 1/1 CRV 20-4 G2-B-80-16 | CRV 20-4C | 1650 | 993 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 329 | 75211367
Hydro-FS-A 1/1 CRV 20-5 G2-B-80-16 | CRV 20-5C | 1650 | 1038 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 333 | 75211107
Hydro-FS-A 1/1 CRV 20-6 G2-B-80-16 | CRV 20-6C | 1650 | 1121 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 349 | 75211402
Hydro-FS-A 1/1 CRV 20-7 G2-B-80-16 | CRV 20-7C | 1650 | 1166 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 353 | 75211377
Hydro-FS-A 1/1 CRV 20-8 G2-B-80-16 | CRV 20-8C | 1650 | 1327 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 465 | 75211403
Hydro-FS-A 1/1 CRV 20-10 G2-B-80-16 | CRV 20-10C | 1650 | 1417 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 475 | 75211404
Hydro-FS-A 1/1 CRV 20-12 G2-B-80-25 | CRV 20-12C | 1650 | 1548 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 15 | 43.9 | звезда-треугольник (SD) | HQQE | 505 | При заказе
Hydro-FS-A 1/1 CRV 20-14 G2-B-80-25 | CRV 20-14C | 1650 | 1638 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 15 | 43.9 | звезда-треугольник (SD) | HQQE | 515 | При заказе
Hydro-FS-A 1/1 CRV 20-17 G2-B-80-25 | CRV 20-17C | 1650 | 1826 | 190 | 585 | 540 | 1589 | 1125 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 | 80 | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HQQE | 565 | При заказе
Hydro-FS-A 1/1 CRV 32-1-1 G2-B-100-16 | CRV 32-1-1C | 1650 | 807 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 1.5 | 21.6 | прямой пуск (DOL) | HQQE | 344 | 75211405
Hydro-FS-A 1/1 CRV 32-1 G2-B-100-16 | CRV 32-1C | 1650 | 807 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 2.2 | 23.9 | прямой пуск (DOL) | HQQE | 350 | 75211406
Hydro-FS-A 1/1 CRV 32-2-2 G2-B-100-16 | CRV 32-2-2C | 1650 | 897 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 3 | 26.4 | прямой пуск (DOL) | HQQE | 364 | 75211407
Hydro-FS-A 1/1 CRV 32-2 G2-B-100-16 | CRV 32-2C | 1650 | 920 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 4 | 23.8 | прямой пуск (DOL) | HQQE | 364 | 75211378
Hydro-FS-A 1/1 CRV 32-3 G2-B-100-16 | CRV 32-3C | 1650 | 1118 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 394 | 75211364
Hydro-FS-A 1/1 CRV 32-4 G2-B-100-16 | CRV 32-4C | 1650 | 1226 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 412 | 75211408
Hydro-FS-A 1/1 CRV 32-5 G2-B-100-16 | CRV 32-5C | 1650 | 1420 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 560 | 75211365
Hydro-FS-A 1/1 CRV 32-6 G2-B-100-16 | CRV 32-6C | 1650 | 1490 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 564 | 75211409
Hydro-FS-A 1/1 CRV 32-7 G2-B-100-16 | CRV 32-7C | 1650 | 1601 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 15 | 43.9 | звезда-треугольник (SD) | HQQE | 584 | 75211410
Hydro-FS-A 1/1 CRV 32-8-2 G2-B-100-16 | CRV 32-8-2C | 1650 | 1671 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 15 | 43.9 | звезда-треугольник (SD) | HQQE | 592 | При заказе
Hydro-FS-A 1/1 CRV 32-8 G2-B-100-16 | CRV 32-8C | 1650 | 1671 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 15 | 43.9 | звезда-треугольник (SD) | HQQE | 592 | При заказе
Hydro-FS-A 1/1 CRV 32-9-2 G2-B-100-25 | CRV 32-9-2C | 1650 | 1794 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HQQE | 650 | При заказе
Hydro-FS-A 1/1 CRV 32-9 G2-B-100-25 | CRV 32-9C | 1650 | 1794 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HQQE | 650 | При заказе
Hydro-FS-A 1/1 CRV 32-10-2 G2-B-100-25 | CRV 32-10-2C | 1650 | 1864 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HQQE | 656 | При заказе
Hydro-FS-A 1/1 CRV 32-10 G2-B-100-25 | CRV 32-10C | 1650 | 1864 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HQQE | 656 | При заказе
Hydro-FS-A 1/1 CRV 32-11-2 G2-B-100-25 | CRV 32-11-2C | 1650 | 1972 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HQQE | 730 | При заказе
Hydro-FS-A 1/1 CRV 32-11 G2-B-100-25 | CRV 32-11C | 1650 | 1972 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HQQE | 730 | При заказе
Hydro-FS-A 1/1 CRV 32-12-2 G2-B-100-25 | CRV 32-12-2C | 1650 | 2042 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HQQE | 736 | При заказе
Hydro-FS-A 1/1 CRV 32-12 G2-B-100-25 | CRV 32-12C | 1650 | 2042 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HQQE | 736 | При заказе
Hydro-FS-A 1/1 CRV 32-13-2 G2-B-100-25 | CRV 32-13-2C | 1650 | 2185 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 866 | При заказе
Hydro-FS-A 1/1 CRV 32-13 G2-B-100-25 | CRV 32-13C | 1650 | 2185 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 866 | При заказе
Hydro-FS-A 1/1 CRV 32-14-2 G2-B-100-25 | CRV 32-14-2C | 1650 | 2255 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 874 | При заказе
Hydro-FS-A 1/1 CRV 32-14 G2-B-100-25 | CRV 32-14C | 1650 | 2255 | 205 | 569 | 605 | 1709 | 1174 | 1960 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 550 | 100 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 874 | При заказе
Hydro-FS-A 1/1 CRV 45-1 G2-B-150-16 | CRV 45-1C | 1650 | 1033 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 150 | 2 | 1 | 1 | 4 | 23.8 | прямой пуск (DOL) | HQQE | 445 | 75211411
Hydro-FS-A 1/1 CRV 45-2-2 G2-B-150-16 | CRV 45-2-2C | 1650 | 1277 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 150 | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 465 | 75211412
Hydro-FS-A 1/1 CRV 45-2 G2-B-150-16 | CRV 45-2C | 1650 | 1315 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 150 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 475 | 75211413
Hydro-FS-A 1/1 CRV 45-3-2 G2-B-150-16 | CRV 45-3-2C | 1650 | 1484 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 150 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 615 | 75211414
Hydro-FS-A 1/1 CRV 45-3 G2-B-150-16 | CRV 45-3C | 1650 | 1484 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 150 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 615 | 75211415
Hydro-FS-A 1/1 CRV 45-4 G2-B-150-16 | CRV 45-4C | 1650 | 1605 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 150 | 2 | 1 | 1 | 15 | 43.9 | звезда-треугольник (SD) | HQQE | 639 | 75211416
Hydro-FS-A 1/1 CRV 45-5 G2-B-150-16 | CRV 45-5C | 1650 | 1738 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 150 | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HQQE | 681 | 75211417
Hydro-FS-A 1/1 CRV 45-6-2 G2-B-100-16 | CRV 45-6-2C | 1650 | 1856 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HQQE | 767 | При заказе
Hydro-FS-A 1/1 CRV 45-6 G2-B-100-25 | CRV 45-6C | 1650 | 1856 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HQQE | 767 | При заказе
Hydro-FS-A 1/1 CRV 45-7-2 G2-B-100-25 | CRV 45-7-2C | 1650 | 2009 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 891 | При заказе
Hydro-FS-A 1/1 CRV 45-7 G2-B-100-25 | CRV 45-7C | 1650 | 2009 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 891 | При заказе
Hydro-FS-A 1/1 CRV 45-8-2 G2-B-100-25 | CRV 45-8-2C | 1650 | 2089 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 899 | При заказе
Hydro-FS-A 1/1 CRV 45-8 G2-B-100-25 | CRV 45-8C | 1650 | 2089 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 899 | При заказе
Hydro-FS-A 1/1 CRV 45-9-2 G2-B-100-25 | CRV 45-9-2C | 1650 | 2169 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 907 | При заказе
Hydro-FS-A 1/1 CRV 45-9 G2-B-100-25 | CRV 45-9C | 1650 | 2169 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HQQE | 947 | При заказе
Hydro-FS-A 1/1 CRV 45-10-2 G2-B-100-25 | CRV 45-10-2C | 1650 | 2249 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HQQE | 955 | При заказе
Hydro-FS-A 1/1 CRV 45-10 G2-B-100-25 | CRV 45-10C | 1650 | 2249 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HQQE | 955 | При заказе
Hydro-FS-A 1/1 CRV 45-11-2 G2-B-100-25 | CRV 45-11-2C | 1650 | 2376 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HQQE | 1087 | При заказе
Hydro-FS-A 1/1 CRV 45-11 G2-B-100-25 | CRV 45-11C | 1650 | 2376 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HQQE | 1087 | При заказе
Hydro-FS-A 1/1 CRV 45-12-2 G2-B-100-25 | CRV 45-12-2C | 1650 | 2456 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HQQE | 1095 | При заказе
Hydro-FS-A 1/1 CRV 45-12 G2-B-100-25 | CRV 45-12C | 1650 | 2456 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HQQE | 1095 | При заказе
Hydro-FS-A 1/1 CRV 45-13-2 G2-B-100-25 | CRV 45-13-2C | 1650 | 2536 | 370 | 686 | 621 | 1888 | 1307 | 1921 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 550 | 100 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HQQE | 1103 | При заказе
Hydro-FS-A 1/1 CRV 64-1 G2-B-200-16 | CRV 64-1C | 1700 | 1109 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 573 | 75211418
Hydro-FS-A 1/1 CRV 64-2-2 G2-B-200-16 | CRV 64-2-2C | 1700 | 1335 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 593 | 75211419
Hydro-FS-A 1/1 CRV 64-2 G2-B-200-16 | CRV 64-2C | 1700 | 1424 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 663 | 75211420
Hydro-FS-A 1/1 CRV 64-3 G2-B-200-16 | CRV 64-3C | 1700 | 1598 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HQQE | 765 | 75211421
Hydro-FS-A 1/1 CRV 64-4-2 G2-B-200-16 | CRV 64-4-2C | 1700 | 1678 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HQQE | 862 | 75211381
Hydro-FS-A 1/1 CRV 64-4-1 G2-B-200-16 | CRV 64-4-1C | 1700 | 1716 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HQQE | 964 | При заказе
Hydro-FS-A 1/1 CRV 64-4 G2-B-200-16 | CRV 64-4C | 1700 | 1716 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HQQE | 964 | При заказе
Hydro-FS-A 1/1 CRV 64-5-2 G2-B-200-16 | CRV 64-5-2C | 1700 | 1869 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 1134 | При заказе
Hydro-FS-A 1/1 CRV 64-5-1 G2-B-200-16 | CRV 64-5-1C | 1700 | 1869 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 1134 | При заказе
Hydro-FS-A 1/1 CRV 64-5 G2-B-200-16 | CRV 64-5C | 1700 | 1869 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 1134 | При заказе
Hydro-FS-A 1/1 CRV 64-6-2 G2-B-200-25 | CRV 64-6-2C | 1700 | 1949 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 1144 | При заказе
Hydro-FS-A 1/1 CRV 64-6-1 G2-B-200-25 | CRV 64-6-1C | 1700 | 1949 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HQQE | 1184 | При заказе
Hydro-FS-A 1/1 CRV 64-6 G2-B-200-25 | CRV 64-6C | 1700 | 1949 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HQQE | 1184 | При заказе
Hydro-FS-A 1/1 CRV 64-7-2 G2-B-200-25 | CRV 64-7-2C | 1700 | 2029 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HQQE | 1194 | При заказе
Hydro-FS-A 1/1 CRV 64-7-1 G2-B-200-25 | CRV 64-7-1C | 1700 | 2029 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HQQE | 1194 | При заказе
Hydro-FS-A 1/1 CRV 64-7 G2-B-200-25 | CRV 64-7C | 1700 | 2076 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HQQE | 1316 | При заказе
Hydro-FS-A 1/1 CRV 64-8-2 G2-B-200-25 | CRV 64-8-2C | 1700 | 2156 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HQQE | 1328 | При заказе
Hydro-FS-A 1/1 CRV 64-8-1 G2-B-200-25 | CRV 64-8-1C | 1700 | 2156 | 390 | 722 | 657 | 1943 | 1379 | 2121 | 1684 | 548 | 588 | 1644 | 150 |  | 12 отв. ø16 | 1000 | 800 | 821 | 650 | 200 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HQQE | 1328 | При заказе
Hydro-FS-A 1/1 CRV 90-1-1 G2-B-200-16 | CRV 90-1-1C | 1700 | 1256 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 645 | При заказе
Hydro-FS-A 1/1 CRV 90-1 G2-B-200-16 | CRV 90-1C | 1700 | 1294 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 649 | При заказе
Hydro-FS-A 1/1 CRV 90-2-2 G2-B-200-16 | CRV 90-2-2C | 1700 | 1447 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HQQE | 735 | При заказе
Hydro-FS-A 1/1 CRV 90-2 G2-B-200-16 | CRV 90-2C | 1700 | 1488 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 15 | 43.9 | звезда-треугольник (SD) | HQQE | 801 | При заказе
Hydro-FS-A 1/1 CRV 90-3-2 G2-B-200-16 | CRV 90-3-2C | 1700 | 1633 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HQQE | 829 | При заказе
Hydro-FS-A 1/1 CRV 90-3 G2-B-200-16 | CRV 90-3C | 1700 | 1671 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HQQE | 937 | При заказе
Hydro-FS-A 1/1 CRV 90-4-2 G2-B-200-16 | CRV 90-4-2C | 1700 | 1836 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 1101 | При заказе
Hydro-FS-A 1/1 CRV 90-4 G2-B-200-16 | CRV 90-4C | 1700 | 1836 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HQQE | 1101 | При заказе
Hydro-FS-A 1/1 CRV 90-5-2 G2-B-200-16 | CRV 90-5-2C | 1700 | 1928 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HQQE | 1155 | При заказе
Hydro-FS-A 1/1 CRV 90-5 G2-B-200-25 | CRV 90-5C | 1700 | 1928 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HQQE | 1155 | При заказе
Hydro-FS-A 1/1 CRV 90-6-2 G2-B-200-25 | CRV 90-6-2C | 1700 | 2067 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HQQE | 1281 | При заказе
Hydro-FS-A 1/1 CRV 90-6 G2-B-200-25 | CRV 90-6C | 1700 | 2067 | 378 | 664 | 730 | 1958 | 1394 | 2121 | 1810 | 548 | 588 | 1750 | 148 | 4 паза R10x40 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HQQE | 1281 | При заказе
Hydro-FS-A 1/1 CRV 120-1 G2-B-200-16 | CRV 120-1C | 1700 | 1480 | 378 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 148 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HUBE | 918 | При заказе
Hydro-FS-A 1/1 CRV 120-2-2 G2-B-200-16 | CRV 120-2-2C | 1700 | 1673 | 378 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 148 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 15 | 43.9 | звезда-треугольник (SD) | HUBE | 948 | При заказе
Hydro-FS-A 1/1 CRV 120-2-1 G2-B-200-16 | CRV 120-2-1C | 1700 | 1726 | 378 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 148 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HUBE | 958 | При заказе
Hydro-FS-A 1/1 CRV 120-2 G2-B-200-16 | CRV 120-2C | 1700 | 1764 | 378 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 148 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HUBE | 1028 | При заказе
Hydro-FS-A 1/1 CRV 120-3-2 G2-B-200-16 | CRV 120-3-2C | 1700 | 1993 | 378 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 148 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HUBE | 1178 | При заказе
Hydro-FS-A 1/1 CRV 120-3-1 G2-B-200-16 | CRV 120-3-1C | 1700 | 1993 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HUBE | 1208 | При заказе
Hydro-FS-A 1/1 CRV 120-3 G2-B-200-16 | CRV 120-3C | 1700 | 1993 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HUBE | 1208 | При заказе
Hydro-FS-A 1/1 CRV 120-4-2 G2-B-200-16 | CRV 120-4-2C | 1700 | 2145 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HUBE | 1288 | При заказе
Hydro-FS-A 1/1 CRV 120-4-1 G2-B-200-16 | CRV 120-4-1C | 1700 | 2145 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HUBE | 1288 | При заказе
Hydro-FS-A 1/1 CRV 120-4 G2-B-200-16 | CRV 120-4C | 1700 | 2194 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HUBE | 1408 | При заказе
Hydro-FS-A 1/1 CRV 120-5-2 G2-B-200-16 | CRV 120-5-2C | 1700 | 2346 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HUBE | 1428 | При заказе
Hydro-FS-A 1/1 CRV 120-5-1 G2-B-200-16 | CRV 120-5-1C | 1700 | 2346 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HUBE | 1428 | При заказе
Hydro-FS-A 1/1 CRV 120-5 G2-B-200-16 | CRV 120-5C | 1700 | 2446 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 55 | 114.5 | звезда-треугольник (SD) | HUBE | 1638 | При заказе
Hydro-FS-A 1/1 CRV 120-6-2 G2-B-200-16 | CRV 120-6-2C | 1700 | 2598 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 55 | 114.5 | звезда-треугольник (SD) | HUBE | 1658 | При заказе
Hydro-FS-A 1/1 CRV 120-6-1 G2-B-200-16 | CRV 120-6-1C | 1700 | 2598 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 55 | 114.5 | звезда-треугольник (SD) | HUBE | 1658 | При заказе
Hydro-FS-A 1/1 CRV 120-6 G2-B-200-16 | CRV 120-6C | 1700 | 2666 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE | 1898 | При заказе
Hydro-FS-A 1/1 CRV 120-7-2 G2-B-200-25 | CRV 120-7-2C | 1700 | 2818 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE | 1918 | При заказе
Hydro-FS-A 1/1 CRV 120-7-1 G2-B-200-25 | CRV 120-7-1C | 1700 | 2818 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE | 1918 | При заказе
Hydro-FS-A 1/1 CRV 120-7 G2-B-200-25 | CRV 120-7C | 1700 | 2818 | 398 | 670 | 748 | 1964 | 1418 | 2171 | 1860 | 548 | 588 | 1790 | 168 | 4 паза R11x45 | 4 отв. ø16 | 1000 | 800 | 821 | 660 | 200 | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE | 1918 | При заказе
Hydro-FS-A 1/1 CRV 150-1-1 G2-B-200-16 | CRV 150-1-1C | [20 empty] | 2 | 1 | 1 | 11 | 36.6 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-1 G2-B-200-16 | CRV 150-1C | [20 empty] | 2 | 1 | 1 | 15 | 43.9 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-2-2 G2-B-200-16 | CRV 150-2-2C | [20 empty] | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-2-1 G2-B-200-16 | CRV 150-2-1C | [20 empty] | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-2 G2-B-200-16 | CRV 150-2C | [20 empty] | 2 | 1 | 1
Hydro-FS-A 1/1 CRV 150-3-2 G2-B-200-16 | CRV 150-3-2C | [20 empty] | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-3-1 G2-B-200-16 | CRV 150-3-1C | [20 empty] | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-3 G2-B-200-16 | CRV 150-3C | [20 empty] | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-4-2 G2-B-200-16 | CRV 150-4-2C | [20 empty] | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-4-1 G2-B-200-16 | CRV 150-4-1C | [20 empty] | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-4 G2-B-200-16 | CRV 150-4C | [20 empty] | 2 | 1 | 1 | 55 | 114.5 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-5-2 G2-B-200-16 | CRV 150-5-2C | [20 empty] | 2 | 1 | 1 | 55 | 114.5 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-5-1 G2-B-200-16 | CRV 150-5-1C | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-5 G2-B-200-16 | CRV 150-5C | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-6-2 G2-B-200-25 | CRV 150-6-2C | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-6-1 G2-B-200-25 | CRV 150-6-1C | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 150-6 G2-B-200-25 | CRV 150-6C | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-1-BI G2-B-200-16 | CRV 200-1CBI | [20 empty] | 2 | 1 | 1 | 18.5 | 50.2 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-1-AI G2-B-200-16 | CRV 200-1CAI | [20 empty] | 2 | 1 | 1 | 22 | 56.5 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-1 G2-B-200-16 | CRV 200-1C | [20 empty] | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-2-BI G2-B-200-16 | CRV 200-2CBI | [20 empty] | 2 | 1 | 1 | 37 | 83.4 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-2-AI G2-B-200-16 | CRV 200-2CAI | [20 empty] | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-2-1-AI G2-B-200-16 | CRV 200-2-1CAI | [20 empty] | 2 | 1 | 1 | 55 | 114.5 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-2 G2-B-200-16 | CRV 200-2C | [20 empty] | 2 | 1 | 1 | 55 | 114.5 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-3-2-BI G2-B-200-16 | CRV 200-3-2CBI | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-3-2-ABI G2-B-200-16 | CRV 200-3-2CABI | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-3-2-AI G2-B-200-16 | CRV 200-3-2CAI | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-3-1-BI G2-B-200-16 | CRV 200-3-1CBI | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-3-1-AI G2-B-200-16 | CRV 200-3-1CAI | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-3 G2-B-200-16 | CRV 200-3C | [20 empty] | 2 | 1 | 1 | 90 | 175.9 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-4-2-BI G2-B-200-16 | CRV 200-4-2CBI | [20 empty] | 2 | 1 | 1 | 90 | 175.9 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-4-2-AI G2-B-200-25 | CRV 200-4-2CAI | [20 empty] | 2 | 1 | 1 | 110 | 211.1 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-4-1-AI G2-B-200-25 | CRV 200-4-1CAI | [20 empty] | 2 | 1 | 1 | 110 | 211.1 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 200-4 G2-B-200-25 | CRV 200-4C | [20 empty] | 2 | 1 | 1 | 110 | 211.1 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 320-1-1 G2-B-200-16 | CRV 320-1-1C | [20 empty] | 2 | 1 | 1 | 30 | 70.9 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 320-1 G2-B-200-16 | CRV 320-1C | [20 empty] | 2 | 1 | 1 | 45 | 96.8 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 320-2-2 G2-B-200-16 | CRV 320-2-2C | [20 empty] | 2 | 1 | 1 | 55 | 114.5 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 320-2-1 G2-B-200-16 | CRV 320-2-1C | [20 empty] | 2 | 1 | 1 | 75 | 149.7 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 320-2 G2-B-200-16 | CRV 320-2C | [20 empty] | 2 | 1 | 1 | 90 | 175.9 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 320-3-2 G2-B-200-16 | CRV 320-3-2C | [20 empty] | 2 | 1 | 1 | 110 | 211.1 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 1/1 CRV 320-3-1 G2-B-200-16 | CRV 320-3-1C | [20 empty] | 2 | 1 | 1 | 110 | 211.1 | звезда-треугольник (SD) | HUBE |  | При заказе
Hydro-FS-A 2/1 CRV 10-1 G2-B-80-16 | CRV 10-1C | 1850 | 613 | 180 | 565 | 520 | 1549 | 1085 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 0.37 | 19.2 | прямой пуск (DOL) | HQQE | 317 | 75211422
Hydro-FS-A 2/1 CRV 10-2 G2-B-80-16 | CRV 10-2C | 1850 | 643 | 180 | 565 | 520 | 1549 | 1085 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 0.75 | 22 | прямой пуск (DOL) | HQQE | 323 | 75211423
Hydro-FS-A 2/1 CRV 10-3 G2-B-80-16 | CRV 10-3C | 1850 | 710 | 180 | 565 | 520 | 1549 | 1085 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 1.1 | 24.4 | прямой пуск (DOL) | HQQE | 335 | 75211424
Hydro-FS-A 2/1 CRV 10-4 G2-B-80-16 | CRV 10-4C | 1850 | 740 | 180 | 565 | 520 | 1549 | 1085 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 1.5 | 27.2 | прямой пуск (DOL) | HQQE | 359 | 75211425
Hydro-FS-A 2/1 CRV 10-5 G2-B-80-16 | CRV 10-5C | 1850 | 822 | 180 | 565 | 520 | 1549 | 1085 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 2.2 | 31.8 | прямой пуск (DOL) | HQQE | 362 | 75211426
Hydro-FS-A 2/1 CRV 10-6 G2-B-80-16 | CRV 10-6C | 1850 | 852 | 180 | 565 | 520 | 1549 | 1085 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 2.2 | 31.8 | прямой пуск (DOL) | HQQE | 365 | 75211386
Hydro-FS-A 2/1 CRV 10-9 G2-B-80-16 | CRV 10-9C | 1850 | 962 | 180 | 565 | 520 | 1549 | 1085 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 3 | 36.8 | прямой пуск (DOL) | HQQE | 389 | 75211427
Hydro-FS-A 2/1 CRV 10-12 G2-B-80-16 | CRV 10-12C | 1850 | 1085 | 180 | 565 | 520 | 1549 | 1085 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 4 | 31.6 | прямой пуск (DOL) | HQQE | 431 | 75211428
Hydro-FS-A 2/1 CRV 10-14 G2-B-80-16 | CRV 10-14C | 1850 | 1226 | 180 | 565 | 520 | 1549 | 1085 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 5.5 | 37.2 | прямой пуск (DOL) | HQQE | 497 | 75211429
Hydro-FS-A 2/1 CRV 10-16 G2-B-80-25 | CRV 10-16C | [20 empty] | 3 | 2 | 1 | 5.5 | 37.2 | прямой пуск (DOL) | HQQE
Hydro-FS-A 2/1 CRV 10-18 G2-B-80-25 | CRV 10-18C | [20 empty] | 3 | 2 | 1 | 7.5 | 44.8 | звезда-треугольник (SD) | HQQE
Hydro-FS-A 2/1 CRV 10-20 G2-B-80-25 | CRV 10-20C | [20 empty] | 3 | 2 | 1 | 7.5 | 44.8 | звезда-треугольник (SD) | HQQE
Hydro-FS-A 2/1 CRV 10-22 G2-B-80-25 | CRV 10-22C | [20 empty] | 3 | 2 | 1 | 7.5 | 44.8 | звезда-треугольник (SD) | HQQE
Hydro-FS-A 2/1 CRV 15-1 G2-B-80-16 | CRV 15-1C | 1850 | 672 | 190 | 585 | 540 | 1589 | 1125 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 1.1 | 24.4 | прямой пуск (DOL) | HQQE | 359 | 75211430
Hydro-FS-A 2/1 CRV 15-2 G2-B-80-16 | CRV 15-2C | 1850 | 769 | 190 | 585 | 540 | 1589 | 1125 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 2.2 | 31.8 | прямой пуск (DOL) | HQQE | 383 | 75211431
Hydro-FS-A 2/1 CRV 15-3 G2-B-80-16 | CRV 15-3C | 1850 | 834 | 190 | 585 | 540 | 1589 | 1125 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 3 | 36.8 | прямой пуск (DOL) | HQQE | 398 | 75211432
Hydro-FS-A 2/1 CRV 15-4 G2-B-80-16 | CRV 15-4C | 1850 | 912 | 190 | 585 | 540 | 1589 | 1125 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 4 | 31.6 | прямой пуск (DOL) | HQQE | 437 | 75211433
Hydro-FS-A 2/1 CRV 15-5 G2-B-80-16 | CRV 15-5C | 1850 | 957 | 190 | 585 | 540 | 1589 | 1125 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 4 | 31.6 | прямой пуск (DOL) | HQQE | 440 | 75211434
Hydro-FS-A 2/1 CRV 15-6 G2-B-80-16 | CRV 15-6C | 1850 | 1083 | 190 | 585 | 540 | 1589 | 1125 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 5.5 | 37.2 | прямой пуск (DOL) | HQQE | 506 | 75211435
Hydro-FS-A 2/1 CRV 15-7 G2-B-80-16 | CRV 15-7C | 1850 | 1128 | 190 | 585 | 540 | 1589 | 1125 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 5.5 | 37.2 | прямой пуск (DOL) | HQQE | 512 | 75211436
Hydro-FS-A 2/1 CRV 15-8 G2-B-80-16 | CRV 15-8C | 1850 | 1211 | 190 | 585 | 540 | 1589 | 1125 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 7.5 | 44.8 | звезда-треугольник (SD) | HQQE | 524 | 75211437
Hydro-FS-A 2/1 CRV 15-9 G2-B-80-16 | CRV 15-9C | 1850 | 1256 | 190 | 585 | 540 | 1589 | 1125 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 7.5 | 44.8 | звезда-треугольник (SD) | HQQE | 527 | 75211438
Hydro-FS-A 2/1 CRV 15-10 G2-B-80-16 | CRV 15-10C | 1850 | 1417 | 190 | 585 | 540 | 1589 | 1125 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 11 | 57.2 | звезда-треугольник (SD) | HQQE | 596 | 75211439
Hydro-FS-A 2/1 CRV 15-12 G2-B-80-25 | CRV 15-12C | [20 empty] | 3 | 2 | 1 | 11 | 57.2 | звезда-треугольник (SD) | HQQE
Hydro-FS-A 2/1 CRV 15-14 G2-B-80-25 | CRV 15-14C | [20 empty] | 3 | 2 | 1 | 11 | 57.2 | звезда-треугольник (SD) | HQQE
Hydro-FS-A 2/1 CRV 15-17 G2-B-80-25 | CRV 15-17C | [20 empty] | 3 | 2 | 1 | 15 | 71.8 | звезда-треугольник (SD) | HQQE
Hydro-FS-A 2/1 CRV 20-1 G2-B-100-16 | CRV 20-1C | 1850 | 672 | 190 | 595 | 550 | 1680 | 1145 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 1.1 | 24.4 | прямой пуск (DOL) | HQQE | 347 | 75211440
Hydro-FS-A 2/1 CRV 20-2 G2-B-100-16 | CRV 20-2C | 1850 | 769 | 190 | 595 | 550 | 1680 | 1145 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 2.2 | 31.8 | прямой пуск (DOL) | HQQE | 380 | 75211441
Hydro-FS-A 2/1 CRV 20-3 G2-B-100-16 | CRV 20-3C | 1850 | 867 | 190 | 595 | 550 | 1680 | 1145 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 4 | 31.6 | прямой пуск (DOL) | HQQE | 422 | 75211442
Hydro-FS-A 2/1 CRV 20-4 G2-B-100-16 | CRV 20-4C | 1850 | 993 | 190 | 595 | 550 | 1680 | 1145 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 5.5 | 37.2 | прямой пуск (DOL) | HQQE | 467 | 75211443
Hydro-FS-A 2/1 CRV 20-5 G2-B-100-16 | CRV 20-5C | 1850 | 1038 | 190 | 595 | 550 | 1680 | 1145 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 5.5 | 37.2 | прямой пуск (DOL) | HQQE | 473 | 75211444
Hydro-FS-A 2/1 CRV 20-6 G2-B-100-16 | CRV 20-6C | 1850 | 1121 | 190 | 595 | 550 | 1680 | 1145 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 7.5 | 44.8 | звезда-треугольник (SD) | HQQE | 497 | 75211445
Hydro-FS-A 2/1 CRV 20-7 G2-B-100-16 | CRV 20-7C | 1850 | 1166 | 190 | 595 | 550 | 1680 | 1145 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 7.5 | 44.8 | звезда-треугольник (SD) | HQQE | 503 | 75211446
Hydro-FS-A 2/1 CRV 20-8 G2-B-100-16 | CRV 20-8C | 1850 | 1327 | 190 | 595 | 550 | 1680 | 1145 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 11 | 57.2 | звезда-треугольник (SD) | HQQE | 671 | 75211447
Hydro-FS-A 2/1 CRV 20-10 G2-B-100-16 | CRV 20-10C | 1850 | 1417 | 190 | 595 | 550 | 1680 | 1145 | 2210 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 450 |  | 3 | 2 | 1 | 11 | 57.2 | звезда-треугольник (SD) | HQQE | 686 | 75211448
Hydro-FS-A 2/1 CRV 20-12 G2-B-100-25 | CRV 20-12C | [20 empty] | 3 | 2 | 1 | 15 | 71.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 20-14 G2-B-100-25 | CRV 20-14C | [20 empty] | 3 | 2 | 1 | 15 | 71.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 20-17 G2-B-100-25 | CRV 20-17C | [20 empty] | 3 | 2 | 1 | 18.5 | 84.4 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-1-1 G2-B-100-16 | CRV 32-1-1C | 1850 | 807 | 205 | 569 | 606 | 1709 | 1175 | 2510 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 550 |  | 3 | 2 | 1 | 1.5 | 27.2 | прямой пуск (DOL) | HQQE | 476 | 75211449
Hydro-FS-A 2/1 CRV 32-1 G2-B-100-16 | CRV 32-1C | 1850 | 807 | 205 | 569 | 606 | 1709 | 1175 | 2510 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 550 |  | 3 | 2 | 1 | 2.2 | 31.8 | прямой пуск (DOL) | HQQE | 485 | 75211450
Hydro-FS-A 2/1 CRV 32-2-2 G2-B-100-16 | CRV 32-2-2C | 1850 | 897 | 205 | 569 | 606 | 1709 | 1175 | 2510 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 550 |  | 3 | 2 | 1 | 3 | 36.8 | прямой пуск (DOL) | HQQE | 506 | 75211451
Hydro-FS-A 2/1 CRV 32-2 G2-B-100-16 | CRV 32-2C | 1850 | 920 | 205 | 569 | 606 | 1709 | 1175 | 2510 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 550 |  | 3 | 2 | 1 | 4 | 31.6 | прямой пуск (DOL) | HQQE | 521 | 75211452
Hydro-FS-A 2/1 CRV 32-3 G2-B-100-16 | CRV 32-3C | 1850 | 1118 | 205 | 569 | 606 | 1709 | 1175 | 2510 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 550 |  | 3 | 2 | 1 | 5.5 | 37.2 | прямой пуск (DOL) | HQQE | 551 | 75211453
Hydro-FS-A 2/1 CRV 32-4 G2-B-100-16 | CRV 32-4C | 1850 | 1226 | 205 | 569 | 606 | 1709 | 1175 | 2510 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 550 |  | 3 | 2 | 1 | 7.5 | 44.8 | звезда-треугольник (SD) | HQQE | 578 | 75211454
Hydro-FS-A 2/1 CRV 32-5 G2-B-100-16 | CRV 32-5C | 1850 | 1420 | 205 | 569 | 606 | 1709 | 1175 | 2510 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 550 |  | 3 | 2 | 1 | 11 | 57.2 | звезда-треугольник (SD) | HQQE | 800 | 75211455
Hydro-FS-A 2/1 CRV 32-6 G2-B-100-16 | CRV 32-6C | 1850 | 1490 | 205 | 569 | 606 | 1709 | 1175 | 2510 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 550 |  | 3 | 2 | 1 | 11 | 57.2 | звезда-треугольник (SD) | HQQE | 806 | 75211456
Hydro-FS-A 2/1 CRV 32-7 G2-B-100-16 | CRV 32-7C | 1850 | 1601 | 205 | 569 | 606 | 1709 | 1175 | 2510 | 427 | нет | нет | 385 | 100 |  | 16 отв. ø16 | 1200 | 800 | 860 | 550 |  | 3 | 2 | 1 | 15 | 71.8 | звезда-треугольник (SD) | HQQE | 836 | 75211457
Hydro-FS-A 2/1 CRV 32-8-2 G2-B-100-16 | CRV 32-8-2C | [20 empty] | 3 | 2 | 1 | 15 | 71.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-8 G2-B-100-16 | CRV 32-8C | [20 empty] | 3 | 2 | 1 | 15 | 71.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-9-2 G2-B-100-25 | CRV 32-9-2C | [20 empty] | 3 | 2 | 1 | 18.5 | 84.4 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-9 G2-B-100-25 | CRV 32-9C | [20 empty] | 3 | 2 | 1 | 18.5 | 84.4 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-10-2 G2-B-100-25 | CRV 32-10-2C | [20 empty] | 3 | 2 | 1 | 18.5 | 84.4 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-10 G2-B-100-25 | CRV 32-10C | [20 empty] | 3 | 2 | 1 | 18.5 | 84.4 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-11-2 G2-B-100-25 | CRV 32-11-2C | [20 empty] | 3 | 2 | 1 | 22 | 97 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-11 G2-B-100-25 | CRV 32-11C | [20 empty] | 3 | 2 | 1 | 22 | 97 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-12-2 G2-B-100-25 | CRV 32-12-2C | [20 empty] | 3 | 2 | 1 | 22 | 97 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-12 G2-B-100-25 | CRV 32-12C | [20 empty] | 3 | 2 | 1 | 22 | 97 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-13-2 G2-B-100-25 | CRV 32-13-2C | [20 empty] | 3 | 2 | 1 | 30 | 125.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-13 G2-B-100-25 | CRV 32-13C | [20 empty] | 3 | 2 | 1 | 30 | 125.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-14-2 G2-B-100-25 | CRV 32-14-2C | [20 empty] | 3 | 2 | 1 | 30 | 125.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 32-14 G2-B-100-25 | CRV 32-14C | [20 empty] | 3 | 2 | 1 | 30 | 125.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-1 G2-B-150-16 | CRV 45-1C | 1900 | 1109 | 390 | 722 | 657 | 1981 | 1379 | 2771 | 1684 | 548 | 588 | 1644 | 150 |  | 16 отв. ø16 | 1200 | 800 | 821 | 650 |  | 3 | 2 | 1 | 4 | 31.6 | прямой пуск (DOL) | HQQE | 906 | 75211465
Hydro-FS-A 2/1 CRV 45-2-2 G2-B-150-16 | CRV 45-2-2C | 1900 | 1335 | 390 | 722 | 657 | 1981 | 1379 | 2771 | 1684 | 548 | 588 | 1644 | 150 |  | 16 отв. ø16 | 1200 | 800 | 821 | 650 |  | 3 | 2 | 1 | 5.5 | 37.2 | прямой пуск (DOL) | HQQE | 936 | 75211466
Hydro-FS-A 2/1 CRV 45-2 G2-B-150-16 | CRV 45-2C | 1900 | 1424 | 390 | 722 | 657 | 1981 | 1379 | 2771 | 1684 | 548 | 588 | 1644 | 150 |  | 16 отв. ø16 | 1200 | 800 | 821 | 650 |  | 3 | 2 | 1 | 7.5 | 44.8 | звезда-треугольник (SD) | HQQE | 1041 | 75211467
Hydro-FS-A 2/1 CRV 45-3-2 G2-B-150-16 | CRV 45-3-2C | 1900 | 1598 | 390 | 722 | 657 | 1981 | 1379 | 2771 | 1684 | 548 | 588 | 1644 | 150 |  | 16 отв. ø16 | 1200 | 800 | 821 | 650 |  | 3 | 2 | 1 | 11 | 57.2 | звезда-треугольник (SD) | HQQE | 1194 | 75211468
Hydro-FS-A 2/1 CRV 45-3 G2-B-150-16 | CRV 45-3C | 1900 | 1678 | 390 | 722 | 657 | 1981 | 1379 | 2771 | 1684 | 548 | 588 | 1644 | 150 |  | 16 отв. ø16 | 1200 | 800 | 821 | 650 |  | 3 | 2 | 1 | 11 | 57.2 | звезда-треугольник (SD) | HQQE | 1203 | 75211469
Hydro-FS-A 2/1 CRV 45-4 G2-B-150-16 | CRV 45-4C | [20 empty] | 3 | 2 | 1 | 15 | 71.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-5 G2-B-150-16 | CRV 45-5C | [20 empty] | 3 | 2 | 1 | 18.5 | 84.4 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-6-2 G2-B-150-16 | CRV 45-6-2C | [20 empty] | 3 | 2 | 1 | 22 | 97 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-6 G2-B-150-25 | CRV 45-6C | [20 empty] | 3 | 2 | 1 | 22 | 97 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-7-2 G2-B-150-25 | CRV 45-7-2C | [20 empty] | 3 | 2 | 1 | 30 | 125.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-7 G2-B-150-25 | CRV 45-7C | [20 empty] | 3 | 2 | 1 | 30 | 125.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-8-2 G2-B-150-25 | CRV 45-8-2C | [20 empty] | 3 | 2 | 1 | 30 | 125.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-8 G2-B-150-25 | CRV 45-8C | [20 empty] | 3 | 2 | 1 | 30 | 125.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-9-2 G2-B-150-25 | CRV 45-9-2C | [20 empty] | 3 | 2 | 1 | 30 | 125.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-9 G2-B-150-25 | CRV 45-9C | [20 empty] | 3 | 2 | 1 | 37 | 150.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-10-2 G2-B-150-25 | CRV 45-10-2C | [20 empty] | 3 | 2 | 1 | 37 | 150.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-10 G2-B-150-25 | CRV 45-10C | [20 empty] | 3 | 2 | 1 | 37 | 150.8 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-11-2 G2-B-150-25 | CRV 45-11-2C | [20 empty] | 3 | 2 | 1 | 45 | 177.6 | звезда-треугольник (SD) | HQQE |  | При заказе
Hydro-FS-A 2/1 CRV 45-11 G2-B-150-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 45-12-2 G2-B-150-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 45-12 G2-B-150-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 45-13-2 G2-B-150-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-1 G2-B-200-16 |  | 1900 | 1109 | 390 | 722 | 657 | 1981 | 1379 | 2771 | 1684 | 548 | 588 | 1644 | 150 |  | 16 отв. ø16 | 1200 | 800 | 821 | 650 |  | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-2-2 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-2 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-3 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-4-2 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-4-1 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-4 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-5-2 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-5-1 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-5 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-6-2 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-6-1 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-6 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-7-2 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-7-1 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-7 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-8-2 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 64-8-1 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-1-1 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-1 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-2-2 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-2 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-3-2 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-3 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-4-2 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-4 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-5-2 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-5 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-6-2 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 90-6 G2-B-200-25 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 120-1 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 120-2-2 G2-B-200-16 | [21 empty] | 3 | 2 | 1
Hydro-FS-A 2/1 CRV 120-2-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-2 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-3-2 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-3-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-3 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-4-2 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-4-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-4 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-5-2 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-5-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-5 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-6-2 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-6-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-6 G2-B-200-16
Hydro-FS-A 2/1 CRV 120-7-2 G2-B-200-25
Hydro-FS-A 2/1 CRV 120-7-1 G2-B-200-25
Hydro-FS-A 2/1 CRV 120-7 G2-B-200-25
Hydro-FS-A 2/1 CRV 150-1-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-2-2 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-2-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-2 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-3-2 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-3-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-3 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-4-2 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-4-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-4 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-5-2 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-5-1 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-5 G2-B-200-16
Hydro-FS-A 2/1 CRV 150-6-2 G2-B-200-25
Hydro-FS-A 2/1 CRV 150-6-1 G2-B-200-25
Hydro-FS-A 2/1 CRV 150-6 G2-B-200-25
Hydro-FS-A 2/1 CRV 200-1-BI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-1-AI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-1 G2-B-250-16
Hydro-FS-A 2/1 CRV 200-2-BI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-2-AI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-2-1-AI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-2 G2-B-250-16
Hydro-FS-A 2/1 CRV 200-3-2-BI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-3-2-ABI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-3-2-AI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-3-1-BI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-3-1-AI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-3 G2-B-250-16
Hydro-FS-A 2/1 CRV 200-4-2-BI G2-B-250-16
Hydro-FS-A 2/1 CRV 200-4-2-AI G2-B-250-25
Hydro-FS-A 2/1 CRV 200-4-1-AI G2-B-250-25
Hydro-FS-A 2/1 CRV 200-4 G2-B-250-25
Hydro-FS-A 2/1 CRV 320-1-1 G2-B-300-16
Hydro-FS-A 2/1 CRV 320-1 G2-B-300-16
Hydro-FS-A 2/1 CRV 320-2-2 G2-B-300-16
Hydro-FS-A 2/1 CRV 320-2-1 G2-B-300-16
Hydro-FS-A 2/1 CRV 320-2 G2-B-300-16
Hydro-FS-A 2/1 CRV 320-3-2 G2-B-300-16
Hydro-FS-A 2/1 CRV 320-3-1 G2-B-300-16

## HFS_NBV
Наименование продукта: | Насос | В | В1 | В2 | Ш1 | Ш2 | Ш3 | Шобщ | Р1 | Р2 | Р3 | Р4 | РП | РВ | ПАЗ | ОТВ-Е | ВШ | ШШ | ШО | К | DN | Общее кол-во | Основа | Резерв | Мощность | Ток | Схема пуска | Торцевое | Масса нетто | Артикул
Hydro-FS-A 1/1 CRV 10-1 G2-B-80-16 | CRV 10-1C | 1650 | 613 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 0.37 | 17.6 | прямой пуск (DOL) | HQQE | 239 | 75211384
Hydro-FS-A 1/1 CRV 10-2 G2-B-80-16 | CRV 10-2C | 1650 | 643 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 0.75 | 19 | прямой пуск (DOL) | HQQE | 243 | 75211387
Hydro-FS-A 1/1 CRV 10-3 G2-B-80-16 | CRV 10-3C | 1650 | 710 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 1.1 | 20.2 | прямой пуск (DOL) | HQQE | 251 | 75211388
Hydro-FS-A 1/1 CRV 10-4 G2-B-80-16 | CRV 10-4C | 1650 | 740 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 1.5 | 21.6 | прямой пуск (DOL) | HQQE | 267 | 75211385
Hydro-FS-A 1/1 CRV 10-5 G2-B-80-16 | CRV 10-5C | 1650 | 822 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 2.2 | 23.9 | прямой пуск (DOL) | HQQE | 269 | 75211371
Hydro-FS-A 1/1 CRV 10-6 G2-B-80-16 | CRV 10-6C | 1650 | 852 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 2.2 | 23.9 | прямой пуск (DOL) | HQQE | 271 | 75211389
Hydro-FS-A 1/1 CRV 10-9 G2-B-80-16 | CRV 10-9C | 1650 | 962 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 3 | 26.4 | прямой пуск (DOL) | HQQE | 287 | 75211376
Hydro-FS-A 1/1 CRV 10-12 G2-B-80-16 | CRV 10-12C | 1650 | 1085 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 4 | 23.8 | прямой пуск (DOL) | HQQE | 315 | 75211390
Hydro-FS-A 1/1 CRV 10-14 G2-B-80-16 | CRV 10-14C | 1650 | 1226 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 359 | 75211391
Hydro-FS-A 1/1 CRV 10-16 G2-B-80-25 | CRV 10-16C | 1650 | 1286 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 5.5 | 26.6 | прямой пуск (DOL) | HQQE | 363 | При заказе
Hydro-FS-A 1/1 CRV 10-18 G2-B-80-25 | CRV 10-18C | 1650 | 1384 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 373 | При заказе
Hydro-FS-A 1/1 CRV 10-20 G2-B-80-25 | CRV 10-20C | 1650 | 1444 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 377 | При заказе
Hydro-FS-A 1/1 CRV 10-22 G2-B-80-25 | CRV 10-22C | 1650 | 1504 | 180 | 565 | 520 | 1549 | 1085 | 1760 | 427 |  |  | 385 | 100 |  | 12 отв. ø16 | 1000 | 800 | 860 | 450 |  | 2 | 1 | 1 | 7.5 | 30.4 | звезда-треугольник (SD) | HQQE | 383 | При заказе

## CRV
Насос | Артикул | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | Q9 | Q10 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8 | H9 | H10 | P1 | P2 | P3 | P4 | P5 | P6 | P7 | P8 | P9 | P10 | NPSH1 | NPSH2 | NPSH3 | NPSH4 | NPSH5 | NPSH6 | NPSH7 | NPSH8 | NPSH9 | NPSH10 | КПД1 | КПД2 | КПД3 | КПД4 | КПД5 | КПД6 | КПД7 | КПД8 | КПД9 | КПД10 | B1 | B2 | D1 | D2 | D3 | D4 | D5 | D6 | a1 | a2 | a3 | a4 | a5 | Hh1 | Hh2 | nxd1 | nxd2 | Давл, бар | Вход | Выход | P2, кВт | I, А △ | I, А Y | pole | Вес (Нетто), кг | Наименование | Торцевое
CRV 1-2C | 74111740 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 12.3244 | 11.5222 | 11.2219 | 10.8476 | 10.3913 | 9.8504 | 9.2276 | 8.5311 | 7.774 | 6.85 | 0.0424 | 0.0726 | 0.0782 | 0.083 | 0.0868 | 0.0896 | 0.0914 | 0.0924 | 0.0926 | 0.0916 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 254 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 21 | CRV 1-2C A-D-E-HQQE-E | HQQE
CRV 1-3C | 74111741 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 17.6825 | 16.8353 | 16.3568 | 15.8576 | 15.2 | 14.4104 | 13.4 | 12.2 | 10.9 | 9.3 | 0.0636 | 0.1089 | 0.1173 | 0.1245 | 0.1302 | 0.1344 | 0.1371 | 0.1386 | 0.1389 | 0.1374 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 272 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 21 | CRV 1-3C A-D-E-HQQE-E | HQQE
CRV 1-4C | 74111742 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 24.9764 | 22.4446 | 21.8184 | 21.0959 | 20.2251 | 19.1523 | 17.8223 | 16.1783 | 14.1619 | 11.87 | 0.0848 | 0.1452 | 0.1564 | 0.166 | 0.1736 | 0.1792 | 0.1828 | 0.1848 | 0.1852 | 0.1832 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 290 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 22 | CRV 1-4C A-D-E-HQQE-E | HQQE
CRV 1-5C | 74111743 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 31.0418 | 28.4 | 27.65 | 26.75 | 25.6607 | 24.3955 | 22.7618 | 20.75 | 18.5 | 15.6 | 0.106 | 0.1815 | 0.1955 | 0.2075 | 0.217 | 0.224 | 0.2285 | 0.231 | 0.2315 | 0.229 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 308 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 22 | CRV 1-5C A-D-E-HQQE-E | HQQE
CRV 1-6C | 74111744 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 37.4935 | 34.036 | 33 | 31.9218 | 30.4042 | 28.7177 | 26.8956 | 24.7 | 22.0738 | 18.99 | 0.1272 | 0.2178 | 0.2346 | 0.249 | 0.2604 | 0.2688 | 0.2742 | 0.2772 | 0.2778 | 0.2748 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 326 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 23 | CRV 1-6C A-D-E-HQQE-E | HQQE
CRV 1-7C | 74111745 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 42.5983 | 39.1018 | 37.9973 | 36.7749 | 35.3624 | 33.6539 | 31.5094 | 28.7552 | 25.4 | 21.4 | 0.1484 | 0.2541 | 0.2737 | 0.2905 | 0.3038 | 0.3136 | 0.3199 | 0.3234 | 0.3241 | 0.3206 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 344 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 23 | CRV 1-7C A-D-E-HQQE-E | HQQE
CRV 1-8C | 74111746 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 48.9774 | 44.9467 | 43.7086 | 42.2201 | 40.4196 | 38.2557 | 35.6869 | 32.6819 | 29.2193 | 25.288 | 0.1696 | 0.2904 | 0.3128 | 0.332 | 0.3472 | 0.3584 | 0.3656 | 0.3696 | 0.3704 | 0.3664 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 362 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.55 | 2.3 | 1.3 | 2 | 24 | CRV 1-8C A-D-E-HQQE-E | HQQE
CRV 1-9C | 74111747 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 53.9414 | 50.6169 | 49.5008 | 48.0067 | 46.0635 | 43.6399 | 40.7489 | 37.4507 | 33.4 | 28.4 | 0.1908 | 0.3267 | 0.3519 | 0.3735 | 0.3906 | 0.4032 | 0.4113 | 0.4158 | 0.4167 | 0.4122 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 380 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.55 | 2.3 | 1.3 | 2 | 24 | CRV 1-9C A-D-E-HQQE-E | HQQE
CRV 1-10C | 74111748 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 59.8933 | 57.0691 | 55.8782 | 54.0363 | 51.6229 | 48.7475 | 45.4592 | 41.655 | 36.9893 | 31.5 | 0.212 | 0.363 | 0.391 | 0.415 | 0.434 | 0.448 | 0.457 | 0.462 | 0.463 | 0.458 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 398 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.55 | 2.3 | 1.3 | 2 | 25 | CRV 1-10C A-D-E-HQQE-E | HQQE
CRV 1-11C | 74111749 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 65.9434 | 62.3536 | 60.75 | 58.811 | 56.4903 | 53.6884 | 50.2267 | 45.8208 | 40.15 | 34 | 0.2332 | 0.3993 | 0.4301 | 0.4565 | 0.4774 | 0.4928 | 0.5027 | 0.5082 | 0.5093 | 0.5038 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 416 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.55 | 2.3 | 1.3 | 2 | 25 | CRV 1-11C A-D-E-HQQE-E | HQQE
CRV 1-12C | 74111750 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 71.9194 | 67.7492 | 66.169 | 64.1763 | 61.6566 | 58.4702 | 54.4417 | 49.3499 | 43.6 | 36.8 | 0.2544 | 0.4356 | 0.4692 | 0.498 | 0.5208 | 0.5376 | 0.5484 | 0.5544 | 0.5556 | 0.5496 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 434 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.75 | 3 | 1.7 | 2 | 26 | CRV 1-12C A-D-E-HQQE-E | HQQE
CRV 1-13C | 74111751 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 77.1078 | 73.5 | 71.6 | 69.2491 | 66.1366 | 62.7427 | 58.9584 | 54 | 47.5 | 40 | 0.2756 | 0.4719 | 0.5083 | 0.5395 | 0.5642 | 0.5824 | 0.5941 | 0.6006 | 0.6019 | 0.5954 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 452 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.75 | 3 | 1.7 | 2 | 26 | CRV 1-13C A-D-E-HQQE-E | HQQE
CRV 1-15C | 74111752 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 88.755 | 85.4259 | 83.2 | 80.448 | 76.803 | 72.6397 | 67.8388 | 61.7747 | 53.8 | 45 | 0.318 | 0.5445 | 0.5865 | 0.6225 | 0.651 | 0.672 | 0.6855 | 0.693 | 0.6945 | 0.687 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 488 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.75 | 3 | 1.7 | 2 | 27 | CRV 1-15C A-D-E-HQQE-E | HQQE
CRV 1-17C | 74111753 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 101.1553 | 96.9175 | 94.534 | 91.1269 | 86.9275 | 82.0787 | 76.4085 | 69.2035 | 59.8 | 49.2 | 0.3604 | 0.6171 | 0.6647 | 0.7055 | 0.7378 | 0.7616 | 0.7769 | 0.7854 | 0.7871 | 0.7786 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 534 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 28 | CRV 1-17C A-D-E-HQQE-E | HQQE
CRV 1-19C | 74111754 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 113.2817 | 108.1332 | 105.2903 | 101.3455 | 96.6979 | 91.576 | 85.1 | 77.1 | 66.5 | 53.6 | 0.4028 | 0.6897 | 0.7429 | 0.7885 | 0.8246 | 0.8512 | 0.8683 | 0.8778 | 0.8797 | 0.8702 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 570 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 29 | CRV 1-19C A-D-E-HQQE-E | HQQE
CRV 1-21C | 74111755 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 125.0765 | 119.1204 | 116.1814 | 112.1872 | 107.3292 | 101.6568 | 94.836 | 85.5 | 73.2 | 58.7 | 0.4452 | 0.7623 | 0.8211 | 0.8715 | 0.9114 | 0.9408 | 0.9597 | 0.9702 | 0.9723 | 0.9618 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 606 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 30 | CRV 1-21C A-D-E-HQQE-E | HQQE
CRV 1-23C | 74111756 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 138.8947 | 129.7789 | 126.1694 | 121.9041 | 116.97 | 111.1475 | 103.3 | 93.5 | 80.5 | 65 | 0.4876 | 0.8349 | 0.8993 | 0.9545 | 0.9982 | 1.0304 | 1.0511 | 1.0626 | 1.0649 | 1.0534 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 642 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 31 | CRV 1-23C A-D-E-HQQE-E | HQQE
CRV 1-25C | 74111757 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 151.2842 | 141.3044 | 137.5122 | 133.0144 | 127.796 | 121.3 | 113.2 | 102.3 | 87.9 | 71.2 | 0.53 | 0.9075 | 0.9775 | 1.0375 | 1.085 | 1.12 | 1.1425 | 1.155 | 1.1575 | 1.145 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 678 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.5 | 5.6 | 3.2 | 2 | 40 | CRV 1-25C A-D-E-HQQE-E | HQQE
CRV 1-27C | 74111758 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 163.4171 | 153.9859 | 149.8219 | 144.1797 | 137.5092 | 130.1121 | 121.4 | 110.8 | 96.5 | 79.76 | 0.5724 | 0.9801 | 1.0557 | 1.1205 | 1.1718 | 1.2096 | 1.2339 | 1.2474 | 1.2501 | 1.2366 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 714 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.5 | 5.6 | 3.2 | 2 | 41 | CRV 1-27C A-D-E-HQQE-E | HQQE
CRV 1-30C | 74111759 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 181.237 | 170.4962 | 166.2002 | 160.4262 | 153.4186 | 145.3181 | 135.86 | 123.2 | 107.98 | 91.23 | 0.636 | 1.089 | 1.173 | 1.245 | 1.302 | 1.344 | 1.371 | 1.386 | 1.389 | 1.374 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 768 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.5 | 5.6 | 3.2 | 2 | 42 | CRV 1-30C A-D-E-HQQE-E | HQQE
CRV 1-33C | 74111760 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 198.571 | 187.6284 | 182.9774 | 176.8665 | 169.3125 | 160.2823 | 149.5316 | 136.4443 | 120.2 | 102.5 | 0.6996 | 1.1979 | 1.2903 | 1.3695 | 1.4322 | 1.4784 | 1.5081 | 1.5246 | 1.5279 | 1.5114 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 832 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 44 | CRV 1-33C A-D-E-HQQE-E | HQQE
CRV 1-36C | 74111761 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 217.2621 | 205.1601 | 199.4774 | 192.3035 | 183.8971 | 174.3795 | 163.4787 | 149.8 | 133.4 | 115 | 0.7632 | 1.3068 | 1.4076 | 1.494 | 1.5624 | 1.6128 | 1.6452 | 1.6632 | 1.6668 | 1.6488 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 886 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 45 | CRV 1-36C A-D-E-HQQE-E | HQQE
CRV 3-2C | 74113744 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 13.8705 | 11.9936 | 10.5979 | 9.0207 | 8.5419 | 8.0296 | 7.495 | 6.9582 | 5.7 | 4.4 | 0.05 | 0.092 | 0.116 | 0.132 | 0.134 | 0.136 | 0.138 | 0.14 | 0.14 | 0.136 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 254 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 21 | CRV 3-2C A-D-E-HQQE-E | HQQE
CRV 3-3C | 74113745 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 19.9994 | 18.0239 | 16.0319 | 13.7313 | 12.9182 | 12.0787 | 11.087 | 10.1463 | 8.006 | 5.7 | 0.075 | 0.138 | 0.174 | 0.198 | 0.201 | 0.204 | 0.207 | 0.21 | 0.21 | 0.204 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 272 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 21 | CRV 3-3C A-D-E-HQQE-E | HQQE
CRV 3-4C | 74113746 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 25.9967 | 24.096 | 21.5426 | 18.4854 | 17.4575 | 16.2997 | 15.14 | 13.8 | 11.0565 | 8.1 | 0.1 | 0.184 | 0.232 | 0.264 | 0.268 | 0.272 | 0.276 | 0.28 | 0.28 | 0.272 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 290 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 22 | CRV 3-4C A-D-E-HQQE-E | HQQE
CRV 3-5C | 74113747 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 32.0195 | 30.006 | 26.907 | 23.0385 | 21.8396 | 20.5185 | 19.0682 | 17.4889 | 13.9949 | 10.2648 | 0.125 | 0.23 | 0.29 | 0.33 | 0.335 | 0.34 | 0.345 | 0.35 | 0.35 | 0.34 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 308 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 22 | CRV 3-5C A-D-E-HQQE-E | HQQE
CRV 3-6C | 74113748 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 38.0185 | 36.0547 | 32.4575 | 27.6747 | 26.0319 | 24.1361 | 22.155 | 20.3262 | 16.4057 | 12 | 0.15 | 0.276 | 0.348 | 0.396 | 0.402 | 0.408 | 0.414 | 0.42 | 0.42 | 0.408 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 326 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.55 | 2.3 | 1.3 | 2 | 23 | CRV 3-6C A-D-E-HQQE-E | HQQE
CRV 3-7C | 74113749 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 45.0214 | 41.95 | 38.8051 | 32.7187 | 30.6766 | 28.6745 | 26.5681 | 24.5 | 19.5259 | 14.4 | 0.175 | 0.322 | 0.406 | 0.462 | 0.469 | 0.476 | 0.483 | 0.49 | 0.49 | 0.476 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 344 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.55 | 2.3 | 1.3 | 2 | 23 | CRV 3-7C A-D-E-HQQE-E | HQQE
CRV 3-8C | 74113750 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 51.0302 | 47.9772 | 43.8724 | 37.1997 | 34.9295 | 32.65 | 30.4 | 27.88 | 22.4752 | 16.8 | 0.2 | 0.368 | 0.464 | 0.528 | 0.536 | 0.544 | 0.552 | 0.56 | 0.56 | 0.544 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 362 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.75 | 3 | 1.7 | 2 | 24 | CRV 3-8C A-D-E-HQQE-E | HQQE
CRV 3-9C | 74113751 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 57.0452 | 52.849 | 48.9455 | 41.5716 | 39.2765 | 36.8459 | 34.2999 | 31.7528 | 26.2698 | 20.0022 | 0.225 | 0.414 | 0.522 | 0.594 | 0.603 | 0.612 | 0.621 | 0.63 | 0.63 | 0.612 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 380 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.75 | 3 | 1.7 | 2 | 24 | CRV 3-9C A-D-E-HQQE-E | HQQE
CRV 3-10C | 74113752 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 63.0417 | 58.9161 | 54.7065 | 46.1522 | 43.3458 | 40.55 | 37.65 | 34.65 | 27.9869 | 20.8 | 0.25 | 0.46 | 0.58 | 0.66 | 0.67 | 0.68 | 0.69 | 0.7 | 0.7 | 0.68 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 398 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.75 | 3 | 1.7 | 2 | 25 | CRV 3-10C A-D-E-HQQE-E | HQQE
CRV 3-11C | 74113753 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 70.0023 | 64.9128 | 59.8139 | 51.0287 | 48.1699 | 45.0551 | 41.9 | 38.7 | 30.8 | 22.5 | 0.275 | 0.506 | 0.638 | 0.726 | 0.737 | 0.748 | 0.759 | 0.77 | 0.77 | 0.748 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 426 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 25 | CRV 3-11C A-D-E-HQQE-E | HQQE
CRV 3-12C | 74113754 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 76.0574 | 70.7328 | 65.4274 | 55.2668 | 52.1659 | 48.8998 | 45.4783 | 41.8912 | 34.0441 | 24.9 | 0.3 | 0.552 | 0.696 | 0.792 | 0.804 | 0.816 | 0.828 | 0.84 | 0.84 | 0.816 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 444 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 26 | CRV 3-12C A-D-E-HQQE-E | HQQE
CRV 3-13C | 74113755 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 82.0647 | 76.8439 | 70.734 | 60.0923 | 56.8656 | 53.4356 | 49.789 | 45.8897 | 37.4 | 27.5 | 0.325 | 0.598 | 0.754 | 0.858 | 0.871 | 0.884 | 0.897 | 0.91 | 0.91 | 0.884 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 462 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 26 | CRV 3-13C A-D-E-HQQE-E | HQQE
CRV 3-15C | 74113756 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 94.0696 | 87.9919 | 81.7089 | 71.7597 | 68.2843 | 64.3356 | 59.9039 | 55.0032 | 45 | 32.7 | 0.375 | 0.69 | 0.87 | 0.99 | 1.005 | 1.02 | 1.035 | 1.05 | 1.05 | 1.02 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 498 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 27 | CRV 3-15C A-D-E-HQQE-E | HQQE
CRV 3-17C | 74113757 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 107.0755 | 100.1462 | 93.0306 | 82.5107 | 78.6831 | 74.2733 | 69.2966 | 64.1 | 52.4 | 38.7 | 0.425 | 0.782 | 0.986 | 1.122 | 1.139 | 1.156 | 1.173 | 1.19 | 1.19 | 1.156 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 534 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.5 | 5.6 | 3.2 | 2 | 28 | CRV 3-17C A-D-E-HQQE-E | HQQE
CRV 3-19C | 74113758 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 118.0959 | 112.0895 | 103.6641 | 91.9262 | 87.6827 | 82.7809 | 77.2337 | 71.9 | 58.9 | 44.5 | 0.475 | 0.874 | 1.102 | 1.254 | 1.273 | 1.292 | 1.311 | 1.33 | 1.33 | 1.292 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 570 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.5 | 5.6 | 3.2 | 2 | 29 | CRV 3-19C A-D-E-HQQE-E | HQQE
CRV 3-21C | 74113759 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 129.1026 | 122.8909 | 114.5716 | 100.663 | 96.1293 | 91.1045 | 85.5408 | 79.3798 | 65.8 | 49.9 | 0.525 | 0.966 | 1.218 | 1.386 | 1.407 | 1.428 | 1.449 | 1.47 | 1.47 | 1.428 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 616 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 30 | CRV 3-21C A-D-E-HQQE-E | HQQE
CRV 3-23C | 74113760 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 142.089 | 134.0142 | 125.0678 | 110.3637 | 105.3075 | 99.6417 | 93.387 | 86.6031 | 73 | 57.09 | 0.575 | 1.058 | 1.334 | 1.518 | 1.541 | 1.564 | 1.587 | 1.61 | 1.61 | 1.564 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 652 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 31 | CRV 3-23C A-D-E-HQQE-E | HQQE
CRV 3-25C | 74113761 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 153.1209 | 145.9543 | 135.0278 | 118.515 | 113.3195 | 107.6246 | 101.3871 | 94.5603 | 79.6 | 61.5 | 0.625 | 1.15 | 1.45 | 1.65 | 1.675 | 1.7 | 1.725 | 1.75 | 1.75 | 1.7 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 688 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 40 | CRV 3-25C A-D-E-HQQE-E | HQQE
CRV 3-27C | 74113762 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 166.1328 | 157.9072 | 145.7755 | 128.7272 | 123.1919 | 117.0284 | 110.2098 | 102.7393 | 87 | 67.7 | 0.675 | 1.242 | 1.566 | 1.782 | 1.809 | 1.836 | 1.863 | 1.89 | 1.89 | 1.836 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 724 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 41 | CRV 3-27C A-D-E-HQQE-E | HQQE
CRV 3-29C | 74113763 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 178.1398 | 168.9954 | 155.8142 | 137.1455 | 131.4325 | 125.1906 | 118.3377 | 110.7741 | 93.6 | 73 | 0.725 | 1.334 | 1.682 | 1.914 | 1.943 | 1.972 | 2.001 | 2.03 | 2.03 | 1.972 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 760 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 42 | CRV 3-29C A-D-E-HQQE-E | HQQE
CRV 3-31C | 74113764 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 189.9959 | 180.0835 | 166.5951 | 146.9071 | 140.6525 | 133.78 | 126.2668 | 118.1079 | 100.3 | 80.5 | 0.775 | 1.426 | 1.798 | 2.046 | 2.077 | 2.108 | 2.139 | 2.17 | 2.17 | 2.108 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 796 | 300 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 3 | 10.4 | 6 | 2 | 44 | CRV 3-31C A-D-E-HQQE-E | HQQE
CRV 3-33C | 74113765 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 202.1258 | 191.1358 | 178.1008 | 156.6187 | 150.0125 | 142.9021 | 135.2435 | 126.9583 | 108.5 | 87.5 | 0.825 | 1.518 | 1.914 | 2.178 | 2.211 | 2.244 | 2.277 | 2.31 | 2.31 | 2.244 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 832 | 300 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 3 | 10.4 | 6 | 2 | 45 | CRV 3-33C A-D-E-HQQE-E | HQQE
CRV 3-36C | 74113766 | 0 | 1.2 | 2 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 4 | 4.4 | 219.9968 | 209.129 | 194.2714 | 172.5438 | 166.0553 | 159.0293 | 151.3337 | 142.7803 | 122.0145 | 98.5 | 0.9 | 1.656 | 2.088 | 2.376 | 2.412 | 2.448 | 2.484 | 2.52 | 2.52 | 2.448 | 1.148 | 1.192 | 1.273 | 1.424 | 1.473 | 1.526 | 1.599 | 1.719 | 2.115 | 2.795 | 0 | 43.44 | 53.97 | 57.97 | 57.95 | 57.5 | 56.59 | 55.19 | 50.77 | 43.93 | 886 | 300 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 3 | 10.4 | 6 | 2 | 47 | CRV 3-36C A-D-E-HQQE-E | HQQE
CRV 5-2C | 74115744 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 15.5029 | 13.55 | 13.1 | 12.1 | 10.8 | 9.35 | 8.5 | 7.65 | 6.75 | 5.83 | 0.08 | 0.172 | 0.188 | 0.212 | 0.232 | 0.246 | 0.252 | 0.256 | 0.258 | 0.26 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 272 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 22 | CRV 5-2C A-D-E-HQQE-E | HQQE
CRV 5-3C | 74115745 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 20.9965 | 18.4905 | 17.8959 | 16.5636 | 14.9775 | 13.0546 | 11.941 | 10.7133 | 9.363 | 7.8833 | 0.12 | 0.258 | 0.282 | 0.318 | 0.348 | 0.369 | 0.378 | 0.384 | 0.387 | 0.39 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 299 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.55 | 2.3 | 1.3 | 2 | 23 | CRV 5-3C A-D-E-HQQE-E | HQQE
CRV 5-4C | 74115746 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 26.7 | 24.1 | 23.4506 | 21.9 | 19.9629 | 17.4 | 15.85 | 14.3 | 12.55 | 10.8 | 0.16 | 0.344 | 0.376 | 0.424 | 0.464 | 0.492 | 0.504 | 0.512 | 0.516 | 0.52 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 326 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.55 | 2.3 | 1.3 | 2 | 23 | CRV 5-4C A-D-E-HQQE-E | HQQE
CRV 5-5C | 74115770 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 32.9979 | 29.7702 | 28.944 | 27.006 | 24.546 | 21.4627 | 19.85 | 17.95 | 16 | 13.8 | 0.2 | 0.43 | 0.47 | 0.53 | 0.58 | 0.615 | 0.63 | 0.64 | 0.645 | 0.65 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 353 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.75 | 3 | 1.7 | 2 | 26 | CRV 5-5C A-D-E-HQQE-E | HQQE
CRV 5-6C | 74115771 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 39.0054 | 36.05 | 35.15 | 32.8842 | 29.9 | 26.4 | 24.4 | 22.25 | 20.1 | 17.75 | 0.24 | 0.516 | 0.564 | 0.636 | 0.696 | 0.738 | 0.756 | 0.768 | 0.774 | 0.78 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 390 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 28 | CRV 5-6C A-D-E-HQQE-E | HQQE
CRV 5-7C | 74115752 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 45.0084 | 42.2195 | 41.3254 | 38.7118 | 35.0864 | 31.05 | 28.75 | 26.25 | 23.55 | 20.8 | 0.28 | 0.602 | 0.658 | 0.742 | 0.812 | 0.861 | 0.882 | 0.896 | 0.903 | 0.91 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 417 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 29 | CRV 5-7C A-D-E-HQQE-E | HQQE
CRV 5-8C | 74115753 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 51.9983 | 48.0535 | 46.9161 | 44.0393 | 40.2129 | 35.6 | 32.9 | 30.1 | 27.1 | 24.0372 | 0.32 | 0.688 | 0.752 | 0.848 | 0.928 | 0.984 | 1.008 | 1.024 | 1.032 | 1.04 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 444 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.1 | 4.2 | 2.4 | 2 | 30 | CRV 5-8C A-D-E-HQQE-E | HQQE
CRV 5-9C | 74115754 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 58.9533 | 54.6831 | 53.35 | 49.6662 | 45.2028 | 39.8466 | 36.8619 | 33.7034 | 30.4065 | 27.0178 | 0.36 | 0.774 | 0.846 | 0.954 | 1.044 | 1.107 | 1.134 | 1.152 | 1.161 | 1.17 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 471 | 240 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.5 | 5.6 | 3.2 | 2 | 36 | CRV 5-9C A-D-E-HQQE-E | HQQE
CRV 5-10C | 74115755 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 66.0006 | 60.6271 | 59.0153 | 54.9973 | 49.9509 | 44.0139 | 40.7645 | 37.3505 | 33.7803 | 30.0513 | 0.4 | 0.86 | 0.94 | 1.06 | 1.16 | 1.23 | 1.26 | 1.28 | 1.29 | 1.3 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 498 | 280 | 150 | 118 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 1.5 | 5.6 | 3.2 | 2 | 37 | CRV 5-10C A-D-E-HQQE-E | HQQE
CRV 5-11C | 74115756 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 72.9424 | 67.175 | 65.6084 | 61.4275 | 55.7657 | 49.2 | 45.4 | 41.4 | 37.2 | 32.9 | 0.44 | 0.946 | 1.034 | 1.166 | 1.276 | 1.353 | 1.386 | 1.408 | 1.419 | 1.43 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 535 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 38 | CRV 5-11C A-D-E-HQQE-E | HQQE
CRV 5-12C | 74115757 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 80.0008 | 73.8956 | 72.4462 | 68.1555 | 61.8431 | 54.4 | 50 | 45.4 | 40.6 | 35.7 | 0.48 | 1.032 | 1.128 | 1.272 | 1.392 | 1.476 | 1.512 | 1.536 | 1.548 | 1.56 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 562 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 39 | CRV 5-12C A-D-E-HQQE-E | HQQE
CRV 5-13C | 74115758 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 86.9248 | 80.2675 | 78.6915 | 74.3662 | 67.9447 | 59.8 | 55.2 | 49.95 | 44.6 | 39.0352 | 0.52 | 1.118 | 1.222 | 1.378 | 1.508 | 1.599 | 1.638 | 1.664 | 1.677 | 1.69 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 589 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 40 | CRV 5-13C A-D-E-HQQE-E | HQQE
CRV 5-14C | 74115759 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 94.0109 | 87.28 | 85.55 | 80.6211 | 73.7618 | 64.6865 | 60 | 54.6 | 48.5 | 42.0789 | 0.56 | 1.204 | 1.316 | 1.484 | 1.624 | 1.722 | 1.764 | 1.792 | 1.806 | 1.82 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 616 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 41 | CRV 5-14C A-D-E-HQQE-E | HQQE
CRV 5-15C | 74115760 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 101.0057 | 94.8571 | 93.219 | 87.85 | 79.8686 | 69.9454 | 64.4268 | 58.5274 | 52.1321 | 45.0078 | 0.6 | 1.29 | 1.41 | 1.59 | 1.74 | 1.845 | 1.89 | 1.92 | 1.935 | 1.95 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 643 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 42 | CRV 5-15C A-D-E-HQQE-E | HQQE
CRV 5-16C | 74115761 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 107.9989 | 101.8759 | 100.0141 | 93.8982 | 85.1422 | 74.7489 | 69.0779 | 62.9578 | 56.0888 | 47.9631 | 0.64 | 1.376 | 1.504 | 1.696 | 1.856 | 1.968 | 2.016 | 2.048 | 2.064 | 2.08 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 670 | 280 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 2.2 | 7.9 | 4.6 | 2 | 43 | CRV 5-16C A-D-E-HQQE-E | HQQE
CRV 5-18C | 74115762 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 120.9258 | 112.7211 | 110.1957 | 103.9258 | 95.6063 | 84.7367 | 78.2184 | 70.9357 | 62.8796 | 54.0642 | 0.72 | 1.548 | 1.692 | 1.908 | 2.088 | 2.214 | 2.268 | 2.304 | 2.322 | 2.34 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 724 | 300 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 3 | 10.4 | 6 | 2 | 46 | CRV 5-18C A-D-E-HQQE-E | HQQE
CRV 5-20C | 74115763 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 133.8271 | 125.8018 | 122.5 | 114.5473 | 105.0978 | 93.2698 | 86.2235 | 78.3413 | 69.6189 | 60.1154 | 0.8 | 1.72 | 1.88 | 2.12 | 2.32 | 2.46 | 2.52 | 2.56 | 2.58 | 2.6 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 778 | 300 | 168 | 127 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 3 | 10.4 | 6 | 2 | 47 | CRV 5-20C A-D-E-HQQE-E | HQQE
CRV 5-22C | 74115764 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 145.9177 | 136.7225 | 133.8432 | 126.2109 | 115.9614 | 102.9733 | 95.3246 | 86.753 | 77.0665 | 65.9948 | 0.88 | 1.892 | 2.068 | 2.332 | 2.552 | 2.706 | 2.772 | 2.816 | 2.838 | 2.86 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 842 | 323 | 200 | 146 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 4 | 7.8 | 4.5 | 2 | 59 | CRV 5-22C A-D-E-HQQE-E | HQQE
CRV 5-24C | 74115765 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 157.9009 | 149.3642 | 146.146 | 137.797 | 126.8707 | 113.0904 | 104.8623 | 95.4686 | 84.5962 | 71.8279 | 0.96 | 2.064 | 2.256 | 2.544 | 2.784 | 2.952 | 3.024 | 3.072 | 3.096 | 3.12 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 896 | 323 | 200 | 146 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 4 | 7.8 | 4.5 | 2 | 61 | CRV 5-24C A-D-E-HQQE-E | HQQE
CRV 5-26C | 74115766 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 170.8851 | 161.4265 | 158.2807 | 149.7209 | 137.9667 | 122.7823 | 113.6955 | 103.3827 | 91.5666 | 77.8641 | 1.04 | 2.236 | 2.444 | 2.756 | 3.016 | 3.198 | 3.276 | 3.328 | 3.354 | 3.38 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 950 | 323 | 200 | 146 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 4 | 7.8 | 4.5 | 2 | 62 | CRV 5-26C A-D-E-HQQE-E | HQQE
CRV 5-29C | 74115767 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 194.8616 | 181.0078 | 176.8265 | 167.9911 | 157.0866 | 141.538 | 131.1642 | 118.6724 | 103.872 | 86.6874 | 1.16 | 2.494 | 2.726 | 3.074 | 3.364 | 3.567 | 3.654 | 3.712 | 3.741 | 3.77 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 1031 | 323 | 200 | 146 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 4 | 7.8 | 4.5 | 2 | 64 | CRV 5-29C A-D-E-HQQE-E | HQQE
CRV 5-32C | 74115768 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 214.8743 | 201.4352 | 197.5779 | 188.1845 | 175.5889 | 157.9699 | 146.4558 | 132.5656 | 115.7741 | 95.4724 | 1.28 | 2.752 | 3.008 | 3.392 | 3.712 | 3.936 | 4.032 | 4.096 | 4.128 | 4.16 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 1139 | 379 | 212 | 160 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 5.5 | 10.6 | 6.1 | 2 | 79 | CRV 5-32C A-D-E-HQQE-E | HQQE
CRV 5-36C | 74115769 | 0 | 2.5 | 3 | 4 | 5 | 6 | 6.5 | 7 | 7.5 | 8 | 240.8671 | 226.8012 | 222.8894 | 211.6954 | 196.822 | 178.2959 | 166.7025 | 152.2928 | 133.4832 | 108.0654 | 1.44 | 3.096 | 3.384 | 3.816 | 4.176 | 4.428 | 4.536 | 4.608 | 4.644 | 4.68 | 0.7 | 0.829 | 0.904 | 1.199 | 1.561 | 1.993 | 2.24 | 2.514 | 2.819 | 3.165 | 0 | 49 | 55.5 | 62.33 | 65.48 | 65.82 | 65.02 | 63.61 | 61.6 | 59.02 | 1247 | 379 | 212 | 160 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 5.5 | 10.6 | 6.1 | 2 | 81 | CRV 5-36C A-D-E-HQQE-E | HQQE
CRV 10-1C | 74117728 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 13.75 | 11.45 | 10.4 | 9.85 | 9.25 | 8.65 | 8 | 7.35 | 6.5995 | 5.82 | 0.102 | 0.242 | 0.2843 | 0.2993 | 0.3105 | 0.3178 | 0.3208 | 0.3192 | 0.3124 | 0.2996 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 306 | 207 | 134 | 112 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 0.37 | 1.6 | 0.9 | 2 | 32 | CRV 10-1C A-D-E-HQQE-E | HQQE
CRV 10-2C | 74117729 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 24 | 21.0089 | 19.1875 | 18.1429 | 17.0089 | 15.7857 | 14.4732 | 13.0714 | 11.5804 | 10 | 0.204 | 0.484 | 0.5686 | 0.5986 | 0.621 | 0.6356 | 0.6416 | 0.6384 | 0.6248 | 0.5992 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 336 | 207 | 134 | 112 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 0.75 | 3 | 1.7 | 2 | 34 | CRV 10-2C A-D-E-HQQE-E | HQQE
CRV 10-3C | 74117730 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 33.8765 | 31.4022 | 29.434 | 28.1817 | 26.7309 | 25.067 | 23.1754 | 21.0414 | 18.6504 | 15.9877 | 0.306 | 0.726 | 0.8529 | 0.8979 | 0.9315 | 0.9534 | 0.9624 | 0.9576 | 0.9372 | 0.8988 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 370 | 240 | 150 | 118 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 1.1 | 4.2 | 2.4 | 2 | 38 | CRV 10-3C A-D-E-HQQE-E | HQQE
CRV 10-4C | 74117731 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 43.8621 | 41.0345 | 38.4039 | 36.7005 | 34.7159 | 32.4336 | 29.8367 | 26.9086 | 23.6325 | 19.9918 | 0.408 | 0.968 | 1.1372 | 1.1972 | 1.242 | 1.2712 | 1.2832 | 1.2768 | 1.2496 | 1.1984 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 400 | 240 | 150 | 118 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 1.5 | 5.6 | 3.2 | 2 | 46 | CRV 10-4C A-D-E-HQQE-E | HQQE
CRV 10-5C | 74117754 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 54.0288 | 49.6684 | 46.2164 | 44.0576 | 41.5879 | 38.7907 | 35.6492 | 32.1467 | 28.2664 | 23.9918 | 0.51 | 1.21 | 1.4215 | 1.4965 | 1.5525 | 1.589 | 1.604 | 1.596 | 1.562 | 1.498 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 442 | 280 | 168 | 127 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 2.2 | 7.9 | 4.6 | 2 | 47 | CRV 10-5C A-D-E-HQQE-E | HQQE
CRV 10-6C | 74117743 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 63.644 | 59.3644 | 55.3634 | 52.7881 | 49.8013 | 46.3821 | 42.5094 | 38.162 | 33.3188 | 27.9588 | 0.612 | 1.452 | 1.7058 | 1.7958 | 1.863 | 1.9068 | 1.9248 | 1.9152 | 1.8744 | 1.7976 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 472 | 280 | 168 | 127 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 2.2 | 7.9 | 4.6 | 2 | 48 | CRV 10-6C A-D-E-HQQE-E | HQQE
CRV 10-7C | 74117744 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 74.716 | 69.435 | 64.3889 | 61.194 | 57.5368 | 53.4065 | 48.7923 | 43.6834 | 38.069 | 31.9383 | 0.714 | 1.694 | 1.9901 | 2.0951 | 2.1735 | 2.2246 | 2.2456 | 2.2344 | 2.1868 | 2.0972 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 502 | 300 | 168 | 127 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 3 | 10.4 | 6 | 2 | 54 | CRV 10-7C A-D-E-HQQE-E | HQQE
CRV 10-8C | 74117745 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 83.7675 | 79.5292 | 74.3981 | 70.9874 | 66.9767 | 62.3389 | 57.0467 | 51.0729 | 44.3901 | 36.9712 | 0.816 | 1.936 | 2.2744 | 2.3944 | 2.484 | 2.5424 | 2.5664 | 2.5536 | 2.4992 | 2.3968 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 532 | 300 | 168 | 127 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 3 | 10.4 | 6 | 2 | 55 | CRV 10-8C A-D-E-HQQE-E | HQQE
CRV 10-9C | 74117746 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 94.8477 | 89.1445 | 84.0926 | 80.6479 | 76.4822 | 71.5144 | 65.6631 | 58.8471 | 50.9852 | 41.9959 | 0.918 | 2.178 | 2.5587 | 2.6937 | 2.7945 | 2.8602 | 2.8872 | 2.8728 | 2.8116 | 2.6964 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 562 | 300 | 168 | 127 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 3 | 10.4 | 6 | 2 | 56 | CRV 10-9C A-D-E-HQQE-E | HQQE
CRV 10-10C | 74117747 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 105.0947 | 99.8089 | 94.7558 | 91.1417 | 86.6499 | 81.1661 | 74.5757 | 66.7643 | 57.6174 | 47.0206 | 1.02 | 2.42 | 2.843 | 2.993 | 3.105 | 3.178 | 3.208 | 3.192 | 3.124 | 2.996 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 602 | 323 | 200 | 146 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 4 | 7.8 | 4.5 | 2 | 68 | CRV 10-10C A-D-E-HQQE-E | HQQE
CRV 10-12C | 74117748 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 124.644 | 119.0251 | 112.4884 | 107.8833 | 102.2478 | 95.4774 | 87.4677 | 78.1143 | 67.3129 | 54.9588 | 1.224 | 2.904 | 3.4116 | 3.5916 | 3.726 | 3.8136 | 3.8496 | 3.8304 | 3.7488 | 3.5952 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 662 | 323 | 200 | 146 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 16 | DN 40 | DN 40 | 4 | 7.8 | 4.5 | 2 | 70 | CRV 10-12C A-D-E-HQQE-E | HQQE
CRV 10-14C | 74117749 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 144.6523 | 138.2796 | 130.3762 | 124.8521 | 118.1383 | 110.1285 | 100.7163 | 89.7957 | 77.2604 | 63.0041 | 1.428 | 3.388 | 3.9802 | 4.1902 | 4.347 | 4.4492 | 4.4912 | 4.4688 | 4.3736 | 4.1944 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 747 | 379 | 212 | 160 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 25 | DN 40 | DN 40 | 5.5 | 10.6 | 6.1 | 2 | 92 | CRV 10-14C A-D-E-HQQE-E | HQQE
CRV 10-16C | 74117750 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 164.6296 | 157.7422 | 148.8021 | 142.4974 | 134.7998 | 125.582 | 114.7168 | 102.0767 | 87.5346 | 70.963 | 1.632 | 3.872 | 4.5488 | 4.7888 | 4.968 | 5.0848 | 5.1328 | 5.1072 | 4.9984 | 4.7936 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 807 | 379 | 212 | 160 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 25 | DN 40 | DN 40 | 5.5 | 10.6 | 6.1 | 2 | 94 | CRV 10-16C A-D-E-HQQE-E | HQQE
CRV 10-18C | 74117751 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 185.9856 | 176.3243 | 167.6887 | 161.4236 | 153.552 | 143.8427 | 132.0645 | 117.9862 | 101.3765 | 82.0041 | 1.836 | 4.356 | 5.1174 | 5.3874 | 5.589 | 5.7204 | 5.7744 | 5.7456 | 5.6232 | 5.3928 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 867 | 417 | 212 | 160 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 25 | DN 40 | DN 40 | 7.5 | 14.4 | 8.3 | 2 | 99 | CRV 10-18C A-D-E-HQQE-E | HQQE
CRV 10-20C | 74117752 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 205.9424 | 194.998 | 186.0359 | 179.4562 | 171.1054 | 160.7043 | 147.9739 | 132.6352 | 114.4091 | 93.0165 | 2.04 | 4.84 | 5.686 | 5.986 | 6.21 | 6.356 | 6.416 | 6.384 | 6.248 | 5.992 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 927 | 417 | 212 | 160 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 25 | DN 40 | DN 40 | 7.5 | 14.4 | 8.3 | 2 | 101 | CRV 10-20C A-D-E-HQQE-E | HQQE
CRV 10-22C | 74117753 | 0 | 5 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 227.1749 | 213.6385 | 204.4502 | 197.7069 | 189.084 | 178.2463 | 164.8587 | 148.5861 | 129.0933 | 106.0453 | 2.244 | 5.324 | 6.2546 | 6.5846 | 6.831 | 6.9916 | 7.0576 | 7.0224 | 6.8728 | 6.5912 | 0.427 | 0.948 | 1.241 | 1.449 | 1.709 | 2.067 | 2.553 | 3.094 | 3.68 | 4.326 | 0 | 54 | 63.51 | 66.12 | 68.06 | 69.23 | 69.5 | 68.65 | 66.3 | 61.81 | 987 | 417 | 212 | 160 | Ø42 | Ø110 | Ø150 | Ø115 | 130 | 195 | 280 | 215 | 284 | 80 | 34 | 4х18х20,5 | 4xØ14 | 25 | DN 40 | DN 40 | 7.5 | 14.4 | 8.3 | 2 | 104 | CRV 10-22C A-D-E-HQQE-E | HQQE
CRV 15-1C | 74118717 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 15.9 | 13.6102 | 12.45 | 11.65 | 11.23 | 10.8 | 9.95 | 9.08 | 8.1136 | 6.9426 | 0.23 | 0.52 | 0.616 | 0.658 | 0.676 | 0.692 | 0.717 | 0.736 | 0.746 | 0.751 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 332 | 240 | 150 | 118 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 1.1 | 4.2 | 2.4 | 2 | 42 | CRV 15-1C A-D-E-HQQE-E | HQQE
CRV 15-2C | 74118718 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 29.0798 | 25.6749 | 23.9836 | 22.7526 | 22.0723 | 21.3472 | 19.7612 | 17.9966 | 16.0637 | 13.9808 | 0.46 | 1.04 | 1.232 | 1.316 | 1.352 | 1.384 | 1.434 | 1.472 | 1.492 | 1.502 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 389 | 280 | 168 | 127 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 2.2 | 7.9 | 4.6 | 2 | 50 | CRV 15-2C A-D-E-HQQE-E | HQQE
CRV 15-3C | 74118712 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 43.0504 | 38.9293 | 36.0747 | 34.0526 | 32.9591 | 31.8094 | 29.3337 | 26.6056 | 23.5958 | 20 | 0.69 | 1.56 | 1.848 | 1.974 | 2.028 | 2.076 | 2.151 | 2.208 | 2.238 | 2.253 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 434 | 300 | 168 | 127 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 3 | 10.4 | 6 | 2 | 55 | CRV 15-3C A-D-E-HQQE-E | HQQE
CRV 15-4C | 74118719 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 57.0963 | 51.2941 | 48.0704 | 45.7174 | 44.3991 | 42.9714 | 39.7361 | 35.8983 | 31.3267 | 26 | 0.92 | 2.08 | 2.464 | 2.632 | 2.704 | 2.768 | 2.868 | 2.944 | 2.984 | 3.004 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 489 | 323 | 200 | 146 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 4 | 7.8 | 4.5 | 2 | 68 | CRV 15-4C A-D-E-HQQE-E | HQQE
CRV 15-5C | 74118720 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 71.0897 | 65.3318 | 61.1198 | 57.9077 | 56.1002 | 54.1519 | 49.8139 | 44.8555 | 39.2381 | 33 | 1.15 | 2.6 | 3.08 | 3.29 | 3.38 | 3.46 | 3.585 | 3.68 | 3.73 | 3.755 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 534 | 323 | 200 | 146 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 4 | 7.8 | 4.5 | 2 | 69 | CRV 15-5C A-D-E-HQQE-E | HQQE
CRV 15-6C | 74118721 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 85.0837 | 79.5238 | 74.3155 | 70.127 | 67.7532 | 65.2064 | 59.6526 | 53.6163 | 47.3003 | 40.1 | 1.38 | 3.12 | 3.696 | 3.948 | 4.056 | 4.152 | 4.302 | 4.416 | 4.476 | 4.506 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 604 | 379 | 212 | 160 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 5.5 | 10.6 | 6.1 | 2 | 91 | CRV 15-6C A-D-E-HQQE-E | HQQE
CRV 15-7C | 74118722 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 98.9691 | 93.8836 | 87.6094 | 82.7974 | 80.1252 | 77.284 | 71.1189 | 64.3519 | 57.0326 | 49.1 | 1.61 | 3.64 | 4.312 | 4.606 | 4.732 | 4.844 | 5.019 | 5.152 | 5.222 | 5.257 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 649 | 379 | 212 | 160 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 5.5 | 10.6 | 6.1 | 2 | 93 | CRV 15-7C A-D-E-HQQE-E | HQQE
CRV 15-8C | 74118723 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 113.0494 | 107.242 | 100.8555 | 95.8124 | 92.9524 | 89.8639 | 82.9927 | 75.182 | 66.4148 | 57 | 1.84 | 4.16 | 4.928 | 5.264 | 5.408 | 5.536 | 5.736 | 5.888 | 5.968 | 6.008 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 694 | 417 | 212 | 160 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 7.5 | 14.4 | 8.3 | 2 | 97 | CRV 15-8C A-D-E-HQQE-E | HQQE
CRV 15-9C | 74118724 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 127.0958 | 121.3623 | 113.6841 | 107.778 | 104.4986 | 101.0134 | 93.4617 | 85.1941 | 76.282 | 66 | 2.07 | 4.68 | 5.544 | 5.922 | 6.084 | 6.228 | 6.453 | 6.624 | 6.714 | 6.759 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 739 | 417 | 212 | 160 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 7.5 | 14.4 | 8.3 | 2 | 98 | CRV 15-9C A-D-E-HQQE-E | HQQE
CRV 15-10C | 74118725 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 141.0051 | 135.3876 | 128.3176 | 122.5568 | 119.239 | 115.6215 | 107.4619 | 98.0284 | 87.271 | 75.8 | 2.3 | 5.2 | 6.16 | 6.58 | 6.76 | 6.92 | 7.17 | 7.36 | 7.46 | 7.51 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 869 | 448 | 255 | 178 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 11 | 20.6 | 11.9 | 2 | 141 | CRV 15-10C A-D-E-HQQE-E | HQQE
CRV 15-12C | 74118726 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 168.9944 | 157.571 | 149.5805 | 143.2471 | 139.5934 | 135.5874 | 126.4359 | 115.6271 | 102.9955 | 89 | 2.76 | 6.24 | 7.392 | 7.896 | 8.112 | 8.304 | 8.604 | 8.832 | 8.952 | 9.012 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 959 | 448 | 255 | 178 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 25 | DN 50 | DN 50 | 11 | 20.6 | 11.9 | 2 | 145 | CRV 15-12C A-D-E-HQQE-E | HQQE
CRV 15-14C | 74118727 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 197.0349 | 181.6717 | 172.1626 | 164.8005 | 160.5887 | 155.99 | 145.5327 | 133.2302 | 118.884 | 102.5 | 3.22 | 7.28 | 8.624 | 9.212 | 9.464 | 9.688 | 10.038 | 10.304 | 10.444 | 10.514 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 1049 | 448 | 255 | 178 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 25 | DN 50 | DN 50 | 11 | 20.6 | 11.9 | 2 | 148 | CRV 15-14C A-D-E-HQQE-E | HQQE
CRV 15-17C | 74118728 | 0 | 8.7 | 12 | 14 | 15 | 16 | 18 | 20 | 22 | 24 | 239.2508 | 218.16 | 208 | 199.68 | 195 | 189.5 | 177.5 | 163 | 145.35 | 125 | 3.91 | 8.84 | 10.472 | 11.186 | 11.492 | 11.764 | 12.189 | 12.512 | 12.682 | 12.767 | 0.656 | 0.878 | 1.032 | 1.172 | 1.258 | 1.361 | 1.635 | 2.137 | 2.899 | 4.068 | 0 | 55 | 66.34 | 69.74 | 71.01 | 71.97 | 72.93 | 72.4 | 70.08 | 65.53 | 1184 | 489 | 255 | 178 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 25 | DN 50 | DN 50 | 15 | 27.9 | 16 | 2 | 158 | CRV 15-17C A-D-E-HQQE-E | HQQE
CRV 20-1C | 74119709 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 14.9065 | 13.103 | 12.4 | 11.8 | 11.15 | 10.45 | 8.85 | 7.95 | 6.9 | 5.8 | 0.342 | 0.663 | 0.741 | 0.786 | 0.826 | 0.861 | 0.916 | 0.935 | 0.95 | 0.96 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 332 | 240 | 150 | 118 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 1.1 | 4.2 | 2.4 | 2 | 33 | CRV 20-1C A-D-E-HQQE-E | HQQE
CRV 20-2C | 74119710 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 29.1024 | 26.61 | 25.25 | 24.1 | 22.7 | 21.2 | 17.9 | 15.9952 | 14.0842 | 12 | 0.684 | 1.326 | 1.482 | 1.572 | 1.652 | 1.722 | 1.832 | 1.87 | 1.9 | 1.92 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 389 | 280 | 168 | 127 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 2.2 | 7.9 | 4.6 | 2 | 44 | CRV 20-2C A-D-E-HQQE-E | HQQE
CRV 20-3C | 74119711 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 43.077 | 39.6058 | 37.6902 | 36.0733 | 34.1755 | 32.001 | 26.8956 | 24.0287 | 20.9 | 17.3 | 1.026 | 1.989 | 2.223 | 2.358 | 2.478 | 2.583 | 2.748 | 2.805 | 2.85 | 2.88 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 444 | 323 | 200 | 146 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 4 | 7.8 | 4.5 | 2 | 58 | CRV 20-3C A-D-E-HQQE-E | HQQE
CRV 20-4C | 74119720 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 57.0876 | 52.8062 | 50.899 | 48.9874 | 46.5113 | 43.4729 | 35.9267 | 31.6328 | 27.204 | 22.2 | 1.368 | 2.652 | 2.964 | 3.144 | 3.304 | 3.444 | 3.664 | 3.74 | 3.8 | 3.84 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 514 | 379 | 212 | 160 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 5.5 | 10.6 | 6.1 | 2 | 73 | CRV 20-4C A-D-E-HQQE-E | HQQE
CRV 20-5C | 74119712 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 71.0687 | 66.0152 | 63.2684 | 60.9052 | 58.0306 | 54.5647 | 45.5144 | 39.7442 | 33.3 | 26.7 | 1.71 | 3.315 | 3.705 | 3.93 | 4.13 | 4.305 | 4.58 | 4.675 | 4.75 | 4.8 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 559 | 379 | 212 | 160 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 5.5 | 10.6 | 6.1 | 2 | 75 | CRV 20-5C A-D-E-HQQE-E | HQQE
CRV 20-6C | 74119721 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 85.0834 | 79.4178 | 76.1971 | 73.4071 | 69.9976 | 65.87 | 55.0293 | 48.0815 | 40.45 | 32.5 | 2.052 | 3.978 | 4.446 | 4.716 | 4.956 | 5.166 | 5.496 | 5.61 | 5.7 | 5.76 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 604 | 417 | 212 | 160 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 7.5 | 14.4 | 8.3 | 2 | 83 | CRV 20-6C A-D-E-HQQE-E | HQQE
CRV 20-7C | 74119713 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 99.981 | 92.9768 | 88.9974 | 85.7774 | 81.9735 | 77.4298 | 65.301 | 57.2057 | 48.4 | 38.6 | 2.394 | 4.641 | 5.187 | 5.502 | 5.782 | 6.027 | 6.412 | 6.545 | 6.65 | 6.72 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 649 | 417 | 212 | 160 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 7.5 | 14.4 | 8.3 | 2 | 85 | CRV 20-7C A-D-E-HQQE-E | HQQE
CRV 20-8C | 74119722 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 114.0381 | 106.1112 | 101.9316 | 98.5158 | 94.4328 | 89.4942 | 76.0848 | 67.0248 | 56.9 | 45.6 | 2.736 | 5.304 | 5.928 | 6.288 | 6.608 | 6.888 | 7.328 | 7.48 | 7.6 | 7.68 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 779 | 448 | 255 | 178 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 11 | 20.6 | 11.9 | 2 | 141 | CRV 20-8C A-D-E-HQQE-E | HQQE
CRV 20-10C | 74119723 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 141.9606 | 133.0441 | 127.5843 | 123.3408 | 118.4438 | 112.6564 | 97.0595 | 86.373 | 73.4 | 59 | 3.42 | 6.63 | 7.41 | 7.86 | 8.26 | 8.61 | 9.16 | 9.35 | 9.5 | 9.6 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 869 | 448 | 255 | 178 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 16 | DN 50 | DN 50 | 11 | 20.6 | 11.9 | 2 | 146 | CRV 20-10C A-D-E-HQQE-E | HQQE
CRV 20-12C | 74119724 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 169.9494 | 159.7413 | 153.6028 | 148.7021 | 142.9598 | 136.1264 | 117.8243 | 105.492 | 90.5 | 73.5 | 4.104 | 7.956 | 8.892 | 9.432 | 9.912 | 10.332 | 10.992 | 11.22 | 11.4 | 11.52 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 959 | 489 | 255 | 178 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 25 | DN 50 | DN 50 | 15 | 27.9 | 16 | 2 | 161 | CRV 20-12C A-D-E-HQQE-E | HQQE
CRV 20-14C | 74119725 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 197.9733 | 187.2471 | 181.2499 | 175.9052 | 169.266 | 161.1452 | 139.7069 | 126.0115 | 110.0789 | 90.4 | 4.788 | 9.282 | 10.374 | 11.004 | 11.564 | 12.054 | 12.824 | 13.09 | 13.3 | 13.44 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 1049 | 489 | 255 | 178 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 25 | DN 50 | DN 50 | 15 | 27.9 | 16 | 2 | 166 | CRV 20-14C A-D-E-HQQE-E | HQQE
CRV 20-17C | 74119726 | 0 | 11 | 14 | 16 | 18 | 20 | 24 | 26 | 28 | 30 | 241.9778 | 229.3565 | 222.8699 | 217.289 | 210.3769 | 201.7945 | 177.9948 | 161.8326 | 142.1102 | 118.222 | 5.814 | 11.271 | 12.597 | 13.362 | 14.042 | 14.637 | 15.572 | 15.895 | 16.15 | 16.32 | 0.564 | 0.849 | 1.033 | 1.18 | 1.352 | 1.558 | 2.202 | 2.855 | 3.894 | 5.507 | 0 | 59.5 | 66.77 | 69.53 | 71.43 | 72.42 | 71.25 | 68.73 | 64.52 | 58.16 | 1184 | 542 | 313 | 257 | Ø50 | Ø120 | Ø165 | Ø127 | 130 | 196 | 300 | 215 | 284 | 90 | 34 | 8х18х21,5 | 4xØ14 | 25 | DN 50 | DN 50 | 18.5 | 34.2 | 19.7 | 2 | 191 | CRV 20-17C A-D-E-HQQE-E | HQQE
CRV 32-1-1C | 74121726 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 16.9 | 14.1 | 13.9 | 13.1 | 12.15 | 11.15 | 10.597 | 10.0434 | 8.7394 | 6.9 | 0.425 | 0.954 | 0.986 | 1.101 | 1.2 | 1.276 | 1.309 | 1.331 | 1.352 | 1.324 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 427 | 280 | 168 | 127 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 1.5 | 5.6 | 3.2 | 2 | 67 | CRV 32-1-1C A-D-E-HQQE-E | HQQE
CRV 32-1C | 74121727 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 22.7 | 18.5 | 18.25 | 17.05 | 15.8 | 14.57 | 13.9 | 13.2 | 11.5533 | 9.4865 | 0.714 | 1.175 | 1.208 | 1.333 | 1.45 | 1.557 | 1.608 | 1.651 | 1.722 | 1.73 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 427 | 280 | 168 | 127 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 2.2 | 7.9 | 4.6 | 2 | 70 | CRV 32-1C A-D-E-HQQE-E | HQQE
CRV 32-2-2C | 74121728 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 35.0621 | 28.75 | 28.3 | 26.3 | 24.2 | 21.9 | 20.65 | 19.37 | 16.35 | 13 | 0.85 | 1.908 | 1.972 | 2.202 | 2.4 | 2.552 | 2.618 | 2.662 | 2.704 | 2.648 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 497 | 300 | 168 | 127 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 3 | 10.4 | 6 | 2 | 77 | CRV 32-2-2C A-D-E-HQQE-E | HQQE
CRV 32-2C | 74121729 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 41.1209 | 34.5697 | 34.0902 | 32.0528 | 29.7764 | 27.1976 | 25.775 | 24.2529 | 20.8787 | 16.9 | 1.428 | 2.35 | 2.416 | 2.666 | 2.9 | 3.114 | 3.216 | 3.302 | 3.444 | 3.46 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 497 | 323 | 200 | 146 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 4 | 7.8 | 4.5 | 2 | 83 | CRV 32-2C A-D-E-HQQE-E | HQQE
CRV 32-3-2C | 74121730 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 53.2675 | 45.6999 | 45.099 | 42.4762 | 39.431 | 35.8686 | 33.8636 | 31.6937 | 26.8116 | 20.9271 | 1.564 | 3.083 | 3.18 | 3.535 | 3.85 | 4.109 | 4.226 | 4.313 | 4.426 | 4.378 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 567 | 323 | 200 | 146 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 5.5 | 10.6 | 6.1 | 2 | 92 | CRV 32-3-2C A-D-E-HQQE-E | HQQE
CRV 32-3C | 74121731 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 59.1156 | 52.522 | 51.8979 | 49.0855 | 45.7066 | 41.6792 | 39.3968 | 36.9217 | 31.3524 | 25 | 2.142 | 3.525 | 3.624 | 3.999 | 4.35 | 4.671 | 4.824 | 4.953 | 5.166 | 5.19 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 639 | 379 | 212 | 160 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 5.5 | 10.6 | 6.1 | 2 | 92 | CRV 32-3C A-D-E-HQQE-E | HQQE
CRV 32-4-2C | 74121732 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 71.1786 | 63.7141 | 62.8425 | 59.0621 | 54.8028 | 49.9582 | 47.2509 | 44.3039 | 37.4979 | 29.08 | 2.278 | 4.258 | 4.388 | 4.868 | 5.3 | 5.666 | 5.834 | 5.964 | 6.148 | 6.108 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 709 | 417 | 212 | 160 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 7.5 | 14.4 | 8.3 | 2 | 101 | CRV 32-4-2C A-D-E-HQQE-E | HQQE
CRV 32-4C | 74121733 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 77.1389 | 70.0782 | 69.3138 | 65.7877 | 61.4384 | 56.1684 | 53.1576 | 49.88 | 42.4756 | 34 | 2.856 | 4.7 | 4.832 | 5.332 | 5.8 | 6.228 | 6.432 | 6.604 | 6.888 | 6.92 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 709 | 417 | 212 | 160 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 7.5 | 14.4 | 8.3 | 2 | 101 | CRV 32-4C A-D-E-HQQE-E | HQQE
CRV 32-5-2C | 74121734 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 89.2342 | 81.2578 | 80.2873 | 75.9074 | 70.6722 | 64.436 | 60.8741 | 56.9694 | 47.9591 | 37.0082 | 2.992 | 5.433 | 5.596 | 6.201 | 6.75 | 7.223 | 7.442 | 7.615 | 7.87 | 7.838 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 872 | 448 | 255 | 178 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 11 | 20.6 | 11.9 | 2 | 175 | CRV 32-5-2C A-D-E-HQQE-E | HQQE
CRV 32-5C | 74121725 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 98.0632 | 88.4156 | 87.4204 | 82.8594 | 77.2687 | 70.5133 | 66.6568 | 62.4586 | 52.9697 | 41.9117 | 3.57 | 5.875 | 6.04 | 6.665 | 7.25 | 7.785 | 8.04 | 8.255 | 8.61 | 8.65 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 872 | 448 | 255 | 178 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 11 | 20.6 | 11.9 | 2 | 175 | CRV 32-5C A-D-E-HQQE-E | HQQE
CRV 32-6-2C | 74121735 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 107.2562 | 98.186 | 97.1684 | 92.409 | 86.4226 | 79.043 | 74.7789 | 70.1043 | 59.4404 | 47 | 3.706 | 6.608 | 6.804 | 7.534 | 8.2 | 8.78 | 9.05 | 9.266 | 9.592 | 9.568 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 942 | 448 | 255 | 178 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 11 | 20.6 | 11.9 | 2 | 177 | CRV 32-6-2C A-D-E-HQQE-E | HQQE
CRV 32-6C | 74121736 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 114.3407 | 106.4536 | 105.4804 | 100.8023 | 94.7052 | 86.9724 | 82.4247 | 77.3867 | 65.7315 | 52 | 4.284 | 7.05 | 7.248 | 7.998 | 8.7 | 9.342 | 9.648 | 9.906 | 10.332 | 10.38 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 942 | 448 | 255 | 178 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 11 | 20.6 | 11.9 | 2 | 177 | CRV 32-6C A-D-E-HQQE-E | HQQE
CRV 32-7-2C | 74121737 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 125.1838 | 116.4767 | 115.4173 | 110.3243 | 103.6785 | 95.2336 | 90.2595 | 84.7434 | 71.9616 | 57 | 4.42 | 7.783 | 8.012 | 8.867 | 9.65 | 10.337 | 10.658 | 10.917 | 11.314 | 11.298 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1012 | 489 | 255 | 178 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 15 | 27.9 | 16 | 2 | 187 | CRV 32-7-2C A-D-E-HQQE-E | HQQE
CRV 32-7C | 74121738 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 133.2309 | 124.2835 | 123.2391 | 118.1617 | 111.4001 | 102.6282 | 97.3864 | 91.5197 | 77.7486 | 60.9885 | 4.998 | 8.225 | 8.456 | 9.331 | 10.15 | 10.899 | 11.256 | 11.557 | 12.054 | 12.11 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1012 | 489 | 255 | 178 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 16 | DN 65 | DN 65 | 15 | 27.9 | 16 | 2 | 187 | CRV 32-7C A-D-E-HQQE-E | HQQE
CRV 32-8-2C | 74121739 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 143.1693 | 133.512 | 132.3292 | 126.6223 | 119.1366 | 109.5823 | 103.9388 | 97.6695 | 83.1081 | 66 | 5.134 | 8.958 | 9.22 | 10.2 | 11.1 | 11.894 | 12.266 | 12.568 | 13.036 | 13.028 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1082 | 489 | 255 | 178 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 25 | DN 65 | DN 65 | 15 | 27.9 | 16 | 2 | 191 | CRV 32-8-2C A-D-E-HQQE-E | HQQE
CRV 32-8C | 74121740 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 149.2817 | 140.2887 | 139.1762 | 133.6949 | 126.282 | 116.5626 | 110.7208 | 104.1619 | 88.705 | 70 | 5.712 | 9.4 | 9.664 | 10.664 | 11.6 | 12.456 | 12.864 | 13.208 | 13.776 | 13.84 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1082 | 489 | 255 | 178 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 25 | DN 65 | DN 65 | 15 | 27.9 | 16 | 2 | 191 | CRV 32-8C A-D-E-HQQE-E | HQQE
CRV 32-9-2C | 74121741 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 161.186 | 150.4976 | 149.3477 | 143.6912 | 135.9766 | 125.714 | 119.4743 | 112.4139 | 95.5865 | 75 | 5.848 | 10.133 | 10.428 | 11.533 | 12.55 | 13.451 | 13.874 | 14.219 | 14.758 | 14.758 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1152 | 542 | 313 | 257 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 25 | DN 65 | DN 65 | 18.5 | 34.2 | 19.7 | 2 | 220 | CRV 32-9-2C A-D-E-HQQE-E | HQQE
CRV 32-9C | 74121742 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 167.269 | 158.4987 | 157.402 | 151.8422 | 144.0218 | 133.4293 | 126.9336 | 119.553 | 101.8813 | 80 | 6.426 | 10.575 | 10.872 | 11.997 | 13.05 | 14.013 | 14.472 | 14.859 | 15.498 | 15.57 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1152 | 542 | 313 | 257 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 25 | DN 65 | DN 65 | 18.5 | 34.2 | 19.7 | 2 | 220 | CRV 32-9C A-D-E-HQQE-E | HQQE
CRV 32-10-2C | 74121743 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 179.3103 | 169.1907 | 168.0247 | 162.1182 | 153.7719 | 142.383 | 135.3592 | 127.3486 | 108.0659 | 84 | 6.562 | 11.308 | 11.636 | 12.866 | 14 | 15.008 | 15.482 | 15.87 | 16.48 | 16.488 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1222 | 542 | 313 | 257 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 25 | DN 65 | DN 65 | 18.5 | 34.2 | 19.7 | 2 | 223 | CRV 32-10-2C A-D-E-HQQE-E | HQQE
CRV 32-10C | 74121744 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 185.4149 | 175.8518 | 174.7745 | 169.1759 | 160.9818 | 149.4822 | 142.2709 | 133.967 | 113.7261 | 88.0496 | 7.14 | 11.75 | 12.08 | 13.33 | 14.5 | 15.57 | 16.08 | 16.51 | 17.22 | 17.3 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1222 | 542 | 313 | 257 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 25 | DN 65 | DN 65 | 18.5 | 34.2 | 19.7 | 2 | 223 | CRV 32-10C A-D-E-HQQE-E | HQQE
CRV 32-11-2C | 74121745 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 198.3226 | 185.6273 | 184.4072 | 178.2576 | 169.4999 | 157.3645 | 149.7896 | 141.0816 | 119.8812 | 92.9935 | 7.276 | 12.483 | 12.844 | 14.199 | 15.45 | 16.565 | 17.09 | 17.521 | 18.202 | 18.218 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1292 | 580 | 356 | 270 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 25 | DN 65 | DN 65 | 22 | 40.5 | 23.3 | 2 | 260 | CRV 32-11-2C A-D-E-HQQE-E | HQQE
CRV 32-11C | 74121746 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 204.3263 | 193.6466 | 192.425 | 186.2332 | 177.3715 | 164.9949 | 157.2003 | 148.1701 | 125.876 | 97.0038 | 7.854 | 12.925 | 13.288 | 14.663 | 15.95 | 17.127 | 17.688 | 18.161 | 18.942 | 19.03 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1292 | 580 | 356 | 270 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 25 | DN 65 | DN 65 | 22 | 40.5 | 23.3 | 2 | 260 | CRV 32-11C A-D-E-HQQE-E | HQQE
CRV 32-12-2C | 74121747 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 217.4013 | 203.6922 | 202.4284 | 195.9851 | 186.6362 | 173.4688 | 165.168 | 155.5702 | 132.0275 | 102 | 7.99 | 13.658 | 14.052 | 15.532 | 16.9 | 18.122 | 18.698 | 19.172 | 19.924 | 19.948 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1362 | 580 | 356 | 270 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 25 | DN 65 | DN 65 | 22 | 40.5 | 23.3 | 2 | 263 | CRV 32-12-2C A-D-E-HQQE-E | HQQE
CRV 32-12C | 74121748 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 223.3463 | 211.1534 | 209.852 | 203.1452 | 193.3947 | 179.7453 | 171.1913 | 161.3419 | 137.3291 | 107 | 8.568 | 14.1 | 14.496 | 15.996 | 17.4 | 18.684 | 19.296 | 19.812 | 20.664 | 20.76 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1362 | 580 | 356 | 270 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 25 | DN 65 | DN 65 | 22 | 40.5 | 23.3 | 2 | 263 | CRV 32-12C A-D-E-HQQE-E | HQQE
CRV 32-13-2C | 74121749 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 236.1014 | 221.5843 | 220.1484 | 212.8811 | 202.5002 | 188.1047 | 179.1199 | 168.7936 | 143.666 | 112 | 8.704 | 14.833 | 15.26 | 16.865 | 18.35 | 19.679 | 20.306 | 20.823 | 21.646 | 21.678 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1432 | 653 | 395 | 304 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 30 | DN 65 | DN 65 | 30 | 54.9 | 31.6 | 2 | 328 | CRV 32-13-2C A-D-E-HQQE-E | HQQE
CRV 32-13C | 74121750 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 242.419 | 228.4416 | 227.1305 | 220.3518 | 210.3554 | 196.1235 | 187.1013 | 176.6386 | 150.8829 | 118 | 9.282 | 15.275 | 15.704 | 17.329 | 18.85 | 20.241 | 20.904 | 21.463 | 22.386 | 22.49 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1432 | 653 | 395 | 304 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 30 | DN 65 | DN 65 | 30 | 54.9 | 31.6 | 2 | 328 | CRV 32-13C A-D-E-HQQE-E | HQQE
CRV 32-14-2C | 74121751 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 255.4836 | 239.3283 | 237.9121 | 230.6956 | 220.1851 | 205.2983 | 195.8756 | 184.9529 | 158.0665 | 124 | 9.418 | 16.008 | 16.468 | 18.198 | 19.8 | 21.236 | 21.914 | 22.474 | 23.368 | 23.408 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1502 | 653 | 395 | 304 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 30 | DN 65 | DN 65 | 30 | 54.9 | 31.6 | 2 | 332 | CRV 32-14-2C A-D-E-HQQE-E | HQQE
CRV 32-14C | 74121752 | 0 | 15 | 16 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 260.0305 | 246.3118 | 244.919 | 237.6871 | 227.0323 | 211.9343 | 202.4001 | 191.3724 | 164.326 | 130 | 9.996 | 16.45 | 16.912 | 18.662 | 20.3 | 21.798 | 22.512 | 23.114 | 24.108 | 24.22 | 1.321 | 1.312 | 1.308 | 1.327 | 1.445 | 1.773 | 2.076 | 2.52 | 3.969 | 6.177 | 0 | 60.2 | 63.5 | 71.16 | 74.88 | 76.29 | 76.07 | 75.18 | 71.16 | 63.61 | 1502 | 653 | 395 | 304 | Ø65 | Ø145 | Ø187 |  | 170 | 224 | 320 | 240 | 334 | 105 | 53 | 8xØ18 | 4xØ14 | 30 | DN 65 | DN 65 | 30 | 54.9 | 31.6 | 2 | 332 | CRV 32-14C A-D-E-HQQE-E | HQQE
CRV 45-1-1C | 74122715 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 22.1 | 20.5 | 20.1 | 19.15 | 18.0205 | 16.6962 | 15.1015 | 13.2042 | 11 | 11 | 0.903 | 1.886 | 2.016 | 2.203 | 2.353 | 2.465 | 2.54 | 2.578 | 2.579 | 2.579 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 480 | 300 | 168 | 127 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 80 | DN 80 | 3 | 10.4 | 6 | 2 | 85 | CRV 45-1-1C A-D-E-HQQE-E | HQQE
CRV 45-1C | 74122716 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 26.1 | 24.5 | 24.2 | 23.5 | 22.7 | 21.75 | 20.3 | 18.45 | 16.0119 | 16.0119 | 1.4 | 2.381 | 2.509 | 2.703 | 2.871 | 3.014 | 3.131 | 3.224 | 3.291 | 3.291 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 480 | 323 | 200 | 146 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 80 | DN 80 | 4 | 7.8 | 4.5 | 2 | 91 | CRV 45-1C A-D-E-HQQE-E | HQQE
CRV 45-2-2C | 74122714 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 42 | 40.05 | 39.55 | 37.9 | 35.7698 | 33.1333 | 30.1547 | 26.8016 | 22.6 | 22.6 | 1.806 | 3.772 | 4.032 | 4.406 | 4.706 | 4.93 | 5.08 | 5.156 | 5.158 | 5.158 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 668 | 379 | 212 | 160 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 80 | DN 80 | 5.5 | 10.6 | 6.1 | 2 | 101 | CRV 45-2-2C A-D-E-HQQE-E | HQQE
CRV 45-2C | 74122717 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 51.8927 | 48.7533 | 47.871 | 46.1748 | 44.1581 | 41.7486 | 38.843 | 35.3067 | 30.6 | 30.6 | 2.8 | 4.762 | 5.018 | 5.406 | 5.742 | 6.028 | 6.262 | 6.448 | 6.582 | 6.582 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 668 | 417 | 212 | 160 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 80 | DN 80 | 7.5 | 14.4 | 8.3 | 2 | 106 | CRV 45-2C A-D-E-HQQE-E | HQQE
CRV 45-3-2C | 74122718 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 66.5 | 63.9595 | 63.0324 | 60.9121 | 58.0013 | 54.25 | 49.644 | 44.2047 | 37.9895 | 37.9895 | 3.206 | 6.153 | 6.541 | 7.109 | 7.577 | 7.944 | 8.211 | 8.38 | 8.449 | 8.449 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 806 | 448 | 255 | 178 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 80 | DN 80 | 11 | 20.6 | 11.9 | 2 | 176 | CRV 45-3-2C A-D-E-HQQE-E | HQQE
CRV 45-3C | 74122719 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 77.9966 | 73.3268 | 72.1508 | 69.8015 | 66.8503 | 63.1277 | 58.4245 | 52.4914 | 45.0392 | 45.0392 | 4.2 | 7.143 | 7.527 | 8.109 | 8.613 | 9.042 | 9.393 | 9.672 | 9.873 | 9.873 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 806 | 448 | 255 | 178 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 80 | DN 80 | 11 | 20.6 | 11.9 | 2 | 176 | CRV 45-3C A-D-E-HQQE-E | HQQE
CRV 45-4-2C | 74122720 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 91.8998 | 88.3 | 87.0102 | 83.9814 | 79.9997 | 75.0138 | 69.0047 | 61.9857 | 54.0018 | 54.0018 | 4.606 | 8.534 | 9.05 | 9.812 | 10.448 | 10.958 | 11.342 | 11.604 | 11.74 | 11.74 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 886 | 489 | 255 | 178 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 80 | DN 80 | 15 | 27.9 | 16 | 2 | 188 | CRV 45-4-2C A-D-E-HQQE-E | HQQE
CRV 45-4C | 74122721 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 103.9 | 99.2 | 97.9 | 94.1 | 89.4 | 84.2 | 77.6 | 69.9 | 60 | 60 | 5.6 | 9.524 | 10.036 | 10.812 | 11.484 | 12.056 | 12.524 | 12.896 | 13.164 | 13.164 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 886 | 489 | 255 | 178 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 80 | DN 80 | 15 | 27.9 | 16 | 2 | 188 | CRV 45-4C A-D-E-HQQE-E | HQQE
CRV 45-5-2C | 74122722 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 119 | 114.7 | 113.2 | 108.9 | 103 | 96.2 | 88.4068 | 79.6 | 68.6 | 68.6 | 6.006 | 10.915 | 11.559 | 12.515 | 13.319 | 13.972 | 14.473 | 14.828 | 15.031 | 15.031 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 966 | 542 | 313 | 257 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 80 | DN 80 | 18.5 | 34.2 | 19.7 | 2 | 209 | CRV 45-5-2C A-D-E-HQQE-E | HQQE
CRV 45-5C | 74122723 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 128.5 | 124.4 | 122.5 | 117.9459 | 111.9544 | 105.0486 | 97.1001 | 87.2 | 76.2 | 76.2 | 7 | 11.905 | 12.545 | 13.515 | 14.355 | 15.07 | 15.655 | 16.12 | 16.455 | 16.455 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 966 | 542 | 313 | 257 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 80 | DN 80 | 18.5 | 34.2 | 19.7 | 2 | 209 | CRV 45-5C A-D-E-HQQE-E | HQQE
CRV 45-6-2C | 74122724 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 143.5 | 138.7 | 137.0161 | 131.8088 | 125.4148 | 117.7801 | 108.7899 | 98.2686 | 85.7 | 85.7 | 7.406 | 13.296 | 14.068 | 15.218 | 16.19 | 16.986 | 17.604 | 18.052 | 18.322 | 18.322 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1046 | 580 | 356 | 270 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 25 | DN 80 | DN 80 | 22 | 40.5 | 23.3 | 2 | 252 | CRV 45-6-2C A-D-E-HQQE-E | HQQE
CRV 45-6C | 74122725 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 153.5 | 148.2 | 146.6 | 141.3298 | 134.7543 | 127.039 | 117.9455 | 107.0994 | 93.7 | 93.7 | 8.4 | 14.286 | 15.054 | 16.218 | 17.226 | 18.084 | 18.786 | 19.344 | 19.746 | 19.746 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1046 | 580 | 356 | 270 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 25 | DN 80 | DN 80 | 22 | 40.5 | 23.3 | 2 | 252 | CRV 45-6C A-D-E-HQQE-E | HQQE
CRV 45-7-2C | 74122726 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 169.8214 | 162.7861 | 159.9089 | 154.1556 | 147.11 | 138.5859 | 128.3118 | 115.9303 | 100.9987 | 100.9987 | 8.806 | 15.677 | 16.577 | 17.921 | 19.061 | 20 | 20.735 | 21.276 | 21.613 | 21.613 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1126 | 653 | 395 | 304 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 25 | DN 80 | DN 80 | 30 | 54.9 | 31.6 | 2 | 314 | CRV 45-7-2C A-D-E-HQQE-E | HQQE
CRV 45-7C | 74122727 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 181.1357 | 172.0148 | 169.2527 | 163.4929 | 156.1528 | 147.1085 | 136.2709 | 123.5859 | 109.0345 | 109.0345 | 9.8 | 16.667 | 17.563 | 18.921 | 20.097 | 21.098 | 21.917 | 22.568 | 23.037 | 23.037 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1126 | 653 | 395 | 304 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 25 | DN 80 | DN 80 | 30 | 54.9 | 31.6 | 2 | 314 | CRV 45-7C A-D-E-HQQE-E | HQQE
CRV 45-8-2C | 74122728 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 194.1025 | 186.7024 | 183.949 | 177.847 | 169.6889 | 159.3738 | 146.9002 | 132.366 | 115.9684 | 115.9684 | 10.206 | 18.058 | 19.086 | 20.624 | 21.932 | 23.014 | 23.866 | 24.5 | 24.904 | 24.904 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1206 | 653 | 395 | 304 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 25 | DN 80 | DN 80 | 30 | 54.9 | 31.6 | 2 | 318 | CRV 45-8-2C A-D-E-HQQE-E | HQQE
CRV 45-8C | 74122729 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 204.822 | 196.9607 | 194.415 | 188.3328 | 179.7546 | 168.6749 | 155.3346 | 140.2212 | 123 | 123 | 11.2 | 19.048 | 20.072 | 21.624 | 22.968 | 24.112 | 25.048 | 25.792 | 26.328 | 26.328 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1206 | 653 | 395 | 304 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 25 | DN 80 | DN 80 | 30 | 54.9 | 31.6 | 2 | 318 | CRV 45-8C A-D-E-HQQE-E | HQQE
CRV 45-9-2C | 74122730 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 220.0013 | 212.3018 | 209.15 | 201.9983 | 193.1129 | 182.0722 | 168.595 | 152.3539 | 132.9758 | 132.9758 | 11.606 | 20.439 | 21.595 | 23.327 | 24.803 | 26.028 | 26.997 | 27.724 | 28.195 | 28.195 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1286 | 653 | 395 | 304 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 25 | DN 80 | DN 80 | 30 | 54.9 | 31.6 | 2 | 322 | CRV 45-9-2C A-D-E-HQQE-E | HQQE
CRV 45-9C | 74122731 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 230.8174 | 222.483 | 219.4 | 211.9394 | 202.7226 | 191.2378 | 177.2733 | 160.6119 | 141.0312 | 141.0312 | 12.6 | 21.429 | 22.581 | 24.327 | 25.839 | 27.126 | 28.179 | 29.016 | 29.619 | 29.619 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1286 | 653 | 395 | 304 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 25 | DN 80 | DN 80 | 37 | 67.4 | 38.8 | 2 | 342 | CRV 45-9C A-D-E-HQQE-E | HQQE
CRV 45-10-2C | 74122732 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 248.5001 | 236.9903 | 233.3 | 224.9846 | 215.065 | 202.9057 | 188.0627 | 169.9821 | 148.0005 | 148.0005 | 13.006 | 22.82 | 24.104 | 26.03 | 27.674 | 29.042 | 30.128 | 30.948 | 31.486 | 31.486 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1366 | 653 | 395 | 304 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 33 | DN 80 | DN 80 | 37 | 67.4 | 38.8 | 2 | 346 | CRV 45-10-2C A-D-E-HQQE-E | HQQE
CRV 45-10C | 74122733 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 259.7965 | 249.9333 | 245.6 | 235.839 | 224.86 | 211.9592 | 196.6772 | 178.3378 | 156.0483 | 156.0483 | 14 | 23.81 | 25.09 | 27.03 | 28.71 | 30.14 | 31.31 | 32.24 | 32.91 | 32.91 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1366 | 653 | 395 | 304 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 33 | DN 80 | DN 80 | 37 | 67.4 | 38.8 | 2 | 346 | CRV 45-10C A-D-E-HQQE-E | HQQE
CRV 45-11-2C | 74122734 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 274.4071 | 263.8207 | 259.1002 | 249.9046 | 238.9146 | 225.761 | 209.8358 | 190.2929 | 166.048 | 166.048 | 14.406 | 25.201 | 26.613 | 28.733 | 30.545 | 32.056 | 33.259 | 34.172 | 34.777 | 34.777 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1446 | 700 | 470 | 345 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 33 | DN 80 | DN 80 | 45 | 80.8 | 46.5 | 2 | 412 | CRV 45-11-2C A-D-E-HQQE-E | HQQE
CRV 45-11C | 74122735 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 286.9189 | 270.8508 | 267.0429 | 258.9088 | 248.1792 | 234.5208 | 217.6928 | 197.5471 | 174.0278 | 174.0278 | 15.4 | 26.191 | 27.599 | 29.733 | 31.581 | 33.154 | 34.441 | 35.464 | 36.201 | 36.201 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1446 | 700 | 470 | 345 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 33 | DN 80 | DN 80 | 45 | 80.8 | 46.5 | 2 | 412 | CRV 45-11C A-D-E-HQQE-E | HQQE
CRV 45-12-2C | 74122736 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 300.951 | 288.5088 | 283.869 | 274.4138 | 262.5778 | 248.012 | 230.2716 | 208.8162 | 183.0096 | 183.0096 | 15.806 | 27.582 | 29.122 | 31.436 | 33.416 | 35.07 | 36.39 | 37.396 | 38.068 | 38.068 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1526 | 700 | 470 | 345 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 33 | DN 80 | DN 80 | 45 | 80.8 | 46.5 | 2 | 416 | CRV 45-12-2C A-D-E-HQQE-E | HQQE
CRV 45-12C | 74122737 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 313.8461 | 299.908 | 295.2073 | 285.5578 | 273.3886 | 258.3647 | 240.1005 | 218.1599 | 192.0561 | 192.0561 | 16.8 | 28.572 | 30.108 | 32.436 | 34.452 | 36.168 | 37.572 | 38.688 | 39.492 | 39.492 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1526 | 700 | 470 | 345 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 33 | DN 80 | DN 80 | 45 | 80.8 | 46.5 | 2 | 416 | CRV 45-12C A-D-E-HQQE-E | HQQE
CRV 45-13-2C | 74122738 | 0 | 22 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 327.1952 | 314.0005 | 309.3087 | 299.3206 | 286.3366 | 270.0597 | 250.2284 | 226.6167 | 199.0341 | 199.0341 | 17.206 | 29.963 | 31.631 | 34.139 | 36.287 | 38.084 | 39.521 | 40.62 | 41.359 | 41.359 | 1.134 | 1.38 | 1.42 | 1.551 | 1.805 | 2.162 | 2.65 | 3.3 | 4.166 | 4.166 | 0 | 66.8 | 71.97 | 76.71 | 79.41 | 80 | 79.46 | 76.93 | 72.7 | 72.7 | 1606 | 700 | 470 | 345 | Ø80 | Ø160 | Ø196 |  | 190 | 248 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 33 | DN 80 | DN 80 | 45 | 80.8 | 46.5 | 2 | 420 | CRV 45-13-2C A-D-E-HQQE-E | HQQE
CRV 64-1-1C | 74123712 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 20.9782 | 18.95 | 17.9 | 16.4 | 14.55 | 13.65 | 12.15 | 8.8 | 8.8 | 8.8 | 1.331 | 2.565 | 3.035 | 3.308 | 3.525 | 3.6 | 3.7 | 3.829 | 3.829 | 3.829 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 480 | 323 | 200 | 146 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 4 | 7.8 | 4.5 | 2 | 106 | CRV 64-1-1C A-D-E-HQQE-E | HQQE
CRV 64-1C | 74123713 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 30.1 | 26.65 | 25.1 | 23 | 20.5 | 19.4 | 17.35 | 13.6 | 13.6 | 13.6 | 3.008 | 3.963 | 4.38 | 4.741 | 5.067 | 5.187 | 5.356 | 5.609 | 5.609 | 5.609 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 480 | 379 | 212 | 160 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 5.5 | 10.6 | 6.1 | 2 | 111 | CRV 64-1C A-D-E-HQQE-E | HQQE
CRV 64-2-2C | 74123714 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 41.1192 | 37.0159 | 34.9708 | 32.0037 | 27.85 | 26.0809 | 22.9295 | 17.0017 | 17.0017 | 17.0017 | 2.662 | 5.13 | 6.07 | 6.616 | 7.05 | 7.2 | 7.4 | 7.658 | 7.658 | 7.658 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 668 | 417 | 212 | 160 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 7.5 | 14.4 | 8.3 | 2 | 121 | CRV 64-2-2C A-D-E-HQQE-E | HQQE
CRV 64-2-1C | 74123715 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 52.2027 | 46.9694 | 43.9689 | 40.2613 | 35.7663 | 33.7257 | 30.3816 | 23.9829 | 23.9829 | 23.9829 | 4.339 | 6.528 | 7.415 | 8.049 | 8.592 | 8.787 | 9.056 | 9.438 | 9.438 | 9.438 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 668 | 448 | 255 | 178 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 11 | 20.6 | 11.9 | 2 | 156 | CRV 64-2-1C A-D-E-HQQE-E | HQQE
CRV 64-2C | 74123716 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 61.1689 | 54.8 | 51.5 | 47.4 | 42.4 | 40.3 | 36.7909 | 30.0113 | 30.0113 | 30.0113 | 6.016 | 7.926 | 8.76 | 9.482 | 10.134 | 10.374 | 10.712 | 11.218 | 11.218 | 11.218 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 726 | 448 | 255 | 178 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 11 | 20.6 | 11.9 | 2 | 156 | CRV 64-2C A-D-E-HQQE-E | HQQE
CRV 64-3-2C | 74123717 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 70 | 65.3 | 61.915 | 56.5 | 49.8 | 46.8 | 41.7 | 31.7 | 31.7 | 31.7 | 5.67 | 9.093 | 10.45 | 11.357 | 12.117 | 12.387 | 12.756 | 13.267 | 13.267 | 13.267 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 806 | 489 | 255 | 178 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 15 | 27.9 | 16 | 2 | 196 | CRV 64-3-2C A-D-E-HQQE-E | HQQE
CRV 64-3-1C | 74123718 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 79.8667 | 73.0862 | 68.7987 | 63.1226 | 56.095 | 52.9471 | 47.9277 | 38.7 | 38.7 | 38.7 | 7.347 | 10.491 | 11.795 | 12.79 | 13.659 | 13.974 | 14.412 | 15.047 | 15.047 | 15.047 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 806 | 489 | 255 | 178 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 15 | 27.9 | 16 | 2 | 196 | CRV 64-3-1C A-D-E-HQQE-E | HQQE
CRV 64-3C | 74123719 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 91.0447 | 80.9171 | 76.0822 | 70.2534 | 63.3292 | 60.2374 | 55.2466 | 45.7 | 45.7 | 45.7 | 9.024 | 11.889 | 13.14 | 14.223 | 15.201 | 15.561 | 16.068 | 16.827 | 16.827 | 16.827 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 806 | 542 | 313 | 257 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 18.5 | 34.2 | 19.7 | 2 | 207 | CRV 64-3C A-D-E-HQQE-E | HQQE
CRV 64-4-2C | 74123720 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 100.0018 | 91.9493 | 87.1169 | 79.9664 | 70.6405 | 66.4 | 59.8 | 47.6 | 47.6 | 47.6 | 8.678 | 13.056 | 14.83 | 16.098 | 17.184 | 17.574 | 18.112 | 18.876 | 18.876 | 18.876 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 886 | 542 | 313 | 257 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 18.5 | 34.2 | 19.7 | 2 | 210 | CRV 64-4-2C A-D-E-HQQE-E | HQQE
CRV 64-4-1C | 74123721 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 110.7617 | 99.9366 | 94.1851 | 86.8323 | 77.7116 | 73.5502 | 66.7571 | 54.0036 | 54.0036 | 54.0036 | 10.355 | 14.454 | 16.175 | 17.531 | 18.726 | 19.161 | 19.768 | 20.656 | 20.656 | 20.656 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 886 | 580 | 356 | 270 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 22 | 40.5 | 23.3 | 2 | 261 | CRV 64-4-1C A-D-E-HQQE-E | HQQE
CRV 64-4C | 74123722 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 119.6714 | 106.9439 | 101.1695 | 93.839 | 84.7211 | 80.5524 | 73.746 | 61.0056 | 61.0056 | 61.0056 | 12.032 | 15.852 | 17.52 | 18.964 | 20.268 | 20.748 | 21.424 | 22.436 | 22.436 | 22.436 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 886 | 580 | 356 | 270 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 22 | 40.5 | 23.3 | 2 | 261 | CRV 64-4C A-D-E-HQQE-E | HQQE
CRV 64-5-2C | 74123723 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 130.3281 | 118.8375 | 113.2449 | 105.1994 | 94.2872 | 89.0941 | 80.4472 | 63.9715 | 63.9715 | 63.9715 | 11.686 | 17.019 | 19.21 | 20.839 | 22.251 | 22.761 | 23.468 | 24.485 | 24.485 | 24.485 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 966 | 653 | 395 | 304 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 30 | 54.9 | 31.6 | 2 | 346 | CRV 64-5-2C A-D-E-HQQE-E | HQQE
CRV 64-5-1C | 74123724 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 138.7573 | 127.8701 | 121.1376 | 112.3434 | 101.2145 | 96.0522 | 87.4996 | 70.9697 | 70.9697 | 70.9697 | 13.363 | 18.417 | 20.555 | 22.272 | 23.793 | 24.348 | 25.124 | 26.265 | 26.265 | 26.265 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 966 | 653 | 395 | 304 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 30 | 54.9 | 31.6 | 2 | 346 | CRV 64-5-1C A-D-E-HQQE-E | HQQE
CRV 64-5C | 74123725 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 148.9324 | 136.0078 | 128.7919 | 119.6196 | 108.2363 | 103.0129 | 94.419 | 77.9759 | 77.9759 | 77.9759 | 15.04 | 19.815 | 21.9 | 23.705 | 25.335 | 25.935 | 26.78 | 28.045 | 28.045 | 28.045 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 966 | 653 | 395 | 304 | Ø100 | Ø180 | Ø220 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 30 | 54.9 | 31.6 | 2 | 346 | CRV 64-5C A-D-E-HQQE-E | HQQE
CRV 64-6-2C | 74123726 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 159.8125 | 146.9846 | 139.9097 | 130.3541 | 117.7187 | 111.6744 | 101.4378 | 80.9787 | 80.9787 | 80.9787 | 14.694 | 20.982 | 23.59 | 25.58 | 27.318 | 27.948 | 28.824 | 30.094 | 30.094 | 30.094 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 1046 | 653 | 395 | 304 | Ø100 | Ø190 | Ø235 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 30 | 54.9 | 31.6 | 2 | 351 | CRV 64-6-2C A-D-E-HQQE-E | HQQE
CRV 64-6-1C | 74123727 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 169.7796 | 157.024 | 148.9021 | 138.1958 | 124.6151 | 118.3255 | 107.9358 | 88.0001 | 88.0001 | 88.0001 | 16.371 | 22.38 | 24.935 | 27.013 | 28.86 | 29.535 | 30.48 | 31.874 | 31.874 | 31.874 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 1046 | 653 | 395 | 304 | Ø100 | Ø190 | Ø235 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 37 | 67.4 | 38.8 | 2 | 371 | CRV 64-6-1C A-D-E-HQQE-E | HQQE
CRV 64-6C | 74123728 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 179.0292 | 164.0327 | 155.8837 | 145.2037 | 131.6263 | 125.3282 | 114.9227 | 95.0026 | 95.0026 | 95.0026 | 18.048 | 23.778 | 26.28 | 28.446 | 30.402 | 31.122 | 32.136 | 33.654 | 33.654 | 33.654 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 1046 | 653 | 395 | 304 | Ø100 | Ø190 | Ø235 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 37 | 67.4 | 38.8 | 2 | 371 | CRV 64-6C A-D-E-HQQE-E | HQQE
CRV 64-7-2C | 74123729 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 189.0855 | 175.8395 | 167.4214 | 155.6091 | 140.1329 | 132.9277 | 121.0995 | 98.9931 | 98.9931 | 98.9931 | 17.702 | 24.945 | 27.97 | 30.321 | 32.385 | 33.135 | 34.18 | 35.703 | 35.703 | 35.703 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 1126 | 653 | 395 | 304 | Ø100 | Ø190 | Ø235 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 37 | 67.4 | 38.8 | 2 | 376 | CRV 64-7-2C A-D-E-HQQE-E | HQQE
CRV 64-7-1C | 74123730 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 199.0462 | 185.102 | 175.7581 | 163.1505 | 147.1615 | 139.8476 | 127.9613 | 106.0077 | 106.0077 | 106.0077 | 19.379 | 26.343 | 29.315 | 31.754 | 33.927 | 34.722 | 35.836 | 37.483 | 37.483 | 37.483 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 1126 | 653 | 395 | 304 | Ø100 | Ø190 | Ø235 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 37 | 67.4 | 38.8 | 2 | 376 | CRV 64-7-1C A-D-E-HQQE-E | HQQE
CRV 64-7C | 74123731 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 209.8425 | 192.967 | 182.9822 | 170.2696 | 154.4636 | 147.1884 | 135.1739 | 111.9859 | 111.9859 | 111.9859 | 21.056 | 27.741 | 30.66 | 33.187 | 35.469 | 36.309 | 37.492 | 39.263 | 39.263 | 39.263 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 1126 | 700 | 470 | 345 | Ø100 | Ø190 | Ø235 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 45 | 80.8 | 46.5 | 2 | 437 | CRV 64-7C A-D-E-HQQE-E | HQQE
CRV 64-8-2C | 74123732 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 218.9237 | 203.9031 | 194.217 | 180.9241 | 163.5789 | 155.4462 | 141.9451 | 115.9965 | 115.9965 | 115.9965 | 20.71 | 28.908 | 32.35 | 35.062 | 37.452 | 38.322 | 39.536 | 41.312 | 41.312 | 41.312 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 1206 | 700 | 470 | 345 | Ø100 | Ø190 | Ø235 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 45 | 80.8 | 46.5 | 2 | 443 | CRV 64-8-2C A-D-E-HQQE-E | HQQE
CRV 64-8-1C | 74123733 | 0 | 30 | 40 | 50 | 60 | 64 | 70 | 80 | 80 | 80 | 229.6368 | 214.0303 | 203.0694 | 188.6092 | 170.4659 | 162.16 | 148.5811 | 123.0219 | 123.0219 | 123.0219 | 22.387 | 30.306 | 33.695 | 36.495 | 38.994 | 39.909 | 41.192 | 43.092 | 43.092 | 43.092 | 0.993 | 1.27 | 1.352 | 1.62 | 2.174 | 2.499 | 3.13 | 4.763 | 4.763 | 4.763 | 0 | 58 | 68.9 | 76.2 | 80.89 | 81.94 | 82.52 | 80.34 | 80.34 | 80.34 | 1206 | 700 | 470 | 345 | Ø100 | Ø190 | Ø235 |  | 190 | 245 | 365 | 266 | 366 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 45 | 80.8 | 46.5 | 2 | 443 | CRV 64-8-1C A-D-E-HQQE-E | HQQE
CRV 90-1-1C | 74124702 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 26.0817 | 22.3 | 21.7 | 20.109 | 18.1256 | 15.8947 | 14.6455 | 13.2768 | 10.0642 | 5.9818 | 2.428 | 3.829 | 3.982 | 4.289 | 4.565 | 4.798 | 4.897 | 4.98 | 5.094 | 5.111 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 639 | 379 | 212 | 160 | Ø100 | Ø180 | Ø220 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 5.5 | 10.6 | 6.1 | 2 | 122 | CRV 90-1-1C A-D-E-HQQE-E | HQQE
CRV 90-1C | 74124703 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 35.1461 | 30.5949 | 29.6635 | 27.5751 | 25.1647 | 22.3841 | 20.8328 | 19.1592 | 15.39 | 10.9504 | 4.785 | 5.559 | 5.695 | 5.951 | 6.184 | 6.394 | 6.491 | 6.582 | 6.747 | 6.889 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 639 | 417 | 212 | 160 | Ø100 | Ø180 | Ø220 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 7.5 | 14.4 | 8.3 | 2 | 124 | CRV 90-1C A-D-E-HQQE-E | HQQE
CRV 90-2-2C | 74124704 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 47.9983 | 42.0657 | 41.1033 | 38.8177 | 35.9307 | 32.2852 | 30.125 | 27.7097 | 22.0183 | 15.0107 | 4.856 | 7.658 | 7.964 | 8.578 | 9.13 | 9.596 | 9.794 | 9.96 | 10.188 | 10.222 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 761 | 448 | 255 | 178 | Ø100 | Ø180 | Ø220 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 11 | 20.6 | 11.9 | 2 | 167 | CRV 90-2-2C A-D-E-HQQE-E | HQQE
CRV 90-2C | 74124705 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 66.001 | 57.4 | 56.25 | 52.9331 | 49.2487 | 44.9628 | 42.6257 | 40.1856 | 35.1047 | 29.4 | 9.57 | 11.118 | 11.39 | 11.902 | 12.368 | 12.788 | 12.982 | 13.164 | 13.494 | 13.778 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 761 | 489 | 255 | 178 | Ø100 | Ø180 | Ø220 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 15 | 27.9 | 16 | 2 | 200 | CRV 90-2C A-D-E-HQQE-E | HQQE
CRV 90-3-2C | 74124706 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 80.2897 | 69.5056 | 68.0882 | 64.6791 | 60.3627 | 55.0326 | 51.9738 | 48.6542 | 41.2648 | 32.9738 | 9.641 | 13.217 | 13.659 | 14.529 | 15.314 | 15.99 | 16.285 | 16.542 | 16.935 | 17.111 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 853 | 542 | 313 | 257 | Ø100 | Ø180 | Ø220 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 18.5 | 34.2 | 19.7 | 2 | 214 | CRV 90-3-2C A-D-E-HQQE-E | HQQE
CRV 90-3C | 74124707 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 97.2771 | 85.2786 | 83.2051 | 78.535 | 73.1889 | 67.2314 | 64.0558 | 60.7719 | 53.964 | 46 | 14.355 | 16.677 | 17.085 | 17.853 | 18.552 | 19.182 | 19.473 | 19.746 | 20.241 | 20.667 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 853 | 580 | 356 | 270 | Ø100 | Ø180 | Ø220 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 22 | 40.5 | 23.3 | 2 | 268 | CRV 90-3C A-D-E-HQQE-E | HQQE
CRV 90-4-2C | 74124708 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 112.1992 | 100.3519 | 98.0479 | 92.9139 | 86.9821 | 80.0572 | 76.1364 | 71.8526 | 61.9903 | 50.0011 | 14.426 | 18.776 | 19.354 | 20.48 | 21.498 | 22.384 | 22.776 | 23.124 | 23.682 | 24 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 945 | 653 | 395 | 304 | Ø100 | Ø180 | Ø220 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 30 | 54.9 | 31.6 | 2 | 350 | CRV 90-4-2C A-D-E-HQQE-E | HQQE
CRV 90-4C | 74124709 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 128.259 | 111.9218 | 109.9676 | 105.284 | 99.4053 | 92.2712 | 88.2564 | 83.9744 | 74.7603 | 64.5 | 19.14 | 22.236 | 22.78 | 23.804 | 24.736 | 25.576 | 25.964 | 26.328 | 26.988 | 27.556 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 945 | 653 | 395 | 304 | Ø100 | Ø180 | Ø220 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ18 | 4xØ14 | 16 | DN 100 | DN 100 | 30 | 54.9 | 31.6 | 2 | 350 | CRV 90-4C A-D-E-HQQE-E | HQQE
CRV 90-5-2C | 74124710 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 144.3898 | 128.7356 | 126.0085 | 119.9837 | 113.032 | 104.8474 | 100.1638 | 95.0018 | 82.9449 | 68.0043 | 19.211 | 24.335 | 25.049 | 26.431 | 27.682 | 28.778 | 29.267 | 29.706 | 30.429 | 30.889 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 1037 | 653 | 395 | 304 | Ø100 | Ø190 | Ø235 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 37 | 67.4 | 38.8 | 2 | 377 | CRV 90-5-2C A-D-E-HQQE-E | HQQE
CRV 90-5C | 74124711 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 160.3354 | 142.4192 | 139.7195 | 133.4798 | 125.9944 | 117.1763 | 112.2599 | 107.0104 | 95.5538 | 82.9358 | 23.925 | 27.795 | 28.475 | 29.755 | 30.92 | 31.97 | 32.455 | 32.91 | 33.735 | 34.445 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 1037 | 653 | 395 | 304 | Ø100 | Ø190 | Ø235 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 37 | 67.4 | 38.8 | 2 | 377 | CRV 90-5C A-D-E-HQQE-E | HQQE
CRV 90-6-2C | 74124712 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 176.1478 | 157.6 | 155.4 | 147.632 | 139.1236 | 129.3509 | 123.8541 | 117.8562 | 104.0097 | 87.0102 | 23.996 | 29.894 | 30.744 | 32.382 | 33.866 | 35.172 | 35.758 | 36.288 | 37.176 | 37.778 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 1129 | 700 | 470 | 345 | Ø100 | Ø190 | Ø235 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 45 | 80.8 | 46.5 | 2 | 440 | CRV 90-6-2C A-D-E-HQQE-E | HQQE
CRV 90-6C | 74124713 | 0 | 45 | 50 | 60 | 70 | 80 | 85 | 90 | 100 | 110 | 192.3398 | 171.6561 | 168.0116 | 159.9907 | 150.9726 | 140.8938 | 135.4248 | 129.647 | 117.0817 | 102.5 | 28.71 | 33.354 | 34.17 | 35.706 | 37.104 | 38.364 | 38.946 | 39.492 | 40.482 | 41.334 | 1.018 | 1.125 | 1.137 | 1.298 | 1.652 | 2.205 | 2.562 | 2.979 | 4.013 | 5.363 | 0 | 62 | 66.96 | 73.26 | 77.64 | 79.84 | 80.03 | 79.57 | 76.51 | 70.27 | 1129 | 700 | 470 | 345 | Ø100 | Ø190 | Ø235 |  | 199 | 250 | 380 | 280 | 384 | 140 | 63 | 8xØ22 | 4xØ14 | 25 | DN 100 | DN 100 | 45 | 80.8 | 46.5 | 2 | 440 | CRV 90-6C A-D-E-HQQE-E | HQQE
CRV 120-1C | 74125701 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 22.9184 | 22.1624 | 21.4669 | 20.9624 | 20.3317 | 19.5585 | 18.6263 | 17.5189 | 16.22 | 14.85 | 7.054 | 8.344 | 8.747 | 8.936 | 9.115 | 9.282 | 9.428 | 9.546 | 9.611 | 9.5 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 834 | 448 | 255 | 182 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 11 | 20.6 | 11.9 | 2 | 230 | CRV 120-1C A-D-E-HUBE-E | HUBE
CRV 120-2-2C | 74125703 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 36.7107 | 34.0583 | 32.5923 | 31.712 | 30.7222 | 29.6143 | 28.3798 | 27.0102 | 25.4971 | 23.8319 | 7.534 | 10.87 | 11.92 | 12.424 | 12.908 | 13.366 | 13.784 | 14.146 | 14.398 | 14.286 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 986 | 489 | 255 | 182 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 15 | 27.9 | 16 | 2 | 245 | CRV 120-2-2C A-D-E-HUBE-E | HUBE
CRV 120-2-1C | 74125702 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 42.7817 | 40.7018 | 39.4893 | 38.6219 | 37.5317 | 36.1825 | 34.5378 | 32.5611 | 30.2161 | 27.2 | 10.821 | 13.779 | 14.707 | 15.148 | 15.569 | 15.965 | 16.32 | 16.619 | 16.81 | 16.643 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 986 | 542 | 313 | 257 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 18.5 | 34.2 | 19.7 | 2 | 250 | CRV 120-2-1C A-D-E-HUBE-E | HUBE
CRV 120-2C | 74125704 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 48.2546 | 45.7956 | 44.4417 | 43.5505 | 42.4825 | 41.2125 | 39.7152 | 37.965 | 35.9367 | 33.2 | 14.108 | 16.688 | 17.494 | 17.872 | 18.23 | 18.564 | 18.856 | 19.092 | 19.222 | 19 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 986 | 580 | 356 | 270 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 22 | 40.5 | 23.3 | 2 | 285 | CRV 120-2C A-D-E-HUBE-E | HUBE
CRV 120-3-2C | 74125706 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 58.7979 | 56.807 | 55.0049 | 53.7961 | 52.3542 | 50.6583 | 48.6873 | 46.4205 | 43.8368 | 40.9152 | 14.588 | 19.214 | 20.667 | 21.36 | 22.023 | 22.648 | 23.212 | 23.692 | 24.009 | 23.786 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1142 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 30 | 54.9 | 31.6 | 2 | 360 | CRV 120-3-2C A-D-E-HUBE-E | HUBE
CRV 120-3-1C | 74125705 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 65.1898 | 63.7286 | 61.913 | 60.6299 | 59.0591 | 57.1727 | 54.9425 | 52.3406 | 49.3387 | 45.909 | 17.875 | 22.123 | 23.454 | 24.084 | 24.684 | 25.247 | 25.748 | 26.165 | 26.421 | 26.143 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1142 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 30 | 54.9 | 31.6 | 2 | 360 | CRV 120-3-1C A-D-E-HUBE-E | HUBE
CRV 120-3C | 74125707 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 70.9448 | 69.3341 | 67.5023 | 66.2011 | 64.6007 | 62.6696 | 60.3759 | 57.6881 | 54.5745 | 51.0034 | 21.162 | 25.032 | 26.241 | 26.808 | 27.345 | 27.846 | 28.284 | 28.638 | 28.833 | 28.5 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1142 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 30 | 54.9 | 31.6 | 2 | 360 | CRV 120-3C A-D-E-HUBE-E | HUBE
CRV 120-4-2C | 74125709 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 81.6258 | 80.1 | 77.8194 | 76.115 | 74.0657 | 71.6498 | 68.8458 | 65.6321 | 61.9871 | 57.8893 | 21.642 | 27.558 | 29.414 | 30.296 | 31.138 | 31.93 | 32.64 | 33.238 | 33.62 | 33.286 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1294 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 37 | 67.4 | 38.8 | 2 | 400 | CRV 120-4-2C A-D-E-HUBE-E | HUBE
CRV 120-4-1C | 74125708 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 90.6931 | 87.0171 | 84.2754 | 82.4967 | 80.4094 | 77.986 | 75.1992 | 72.0214 | 68.4252 | 64.3831 | 24.929 | 30.467 | 32.201 | 33.02 | 33.799 | 34.529 | 35.176 | 35.711 | 36.032 | 35.643 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1294 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 37 | 67.4 | 38.8 | 2 | 400 | CRV 120-4-1C A-D-E-HUBE-E | HUBE
CRV 120-4C | 74125710 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 95.8221 | 92.3659 | 89.7435 | 87.9792 | 85.8603 | 83.3474 | 80.401 | 76.9817 | 73.0501 | 68.5668 | 28.216 | 33.376 | 34.988 | 35.744 | 36.46 | 37.128 | 37.712 | 38.184 | 38.444 | 38 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1294 | 702 | 450 | 340 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 45 | 80.8 | 46.5 | 2 | 460 | CRV 120-4C A-D-E-HUBE-E | HUBE
CRV 120-5-2C | 74125712 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 107.859 | 104.4263 | 101.1189 | 98.9003 | 96.2578 | 93.1561 | 89.5597 | 85.4332 | 80.7411 | 75.4482 | 28.696 | 35.902 | 38.161 | 39.232 | 40.253 | 41.212 | 42.068 | 42.784 | 43.231 | 42.786 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1446 | 702 | 450 | 340 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 45 | 80.8 | 46.5 | 2 | 470 | CRV 120-5-2C A-D-E-HUBE-E | HUBE
CRV 120-5-1C | 74125711 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 114.8342 | 110.5124 | 107.277 | 105.1382 | 102.5973 | 99.6132 | 96.1449 | 92.1514 | 87.5917 | 82.4247 | 31.983 | 38.811 | 40.948 | 41.956 | 42.914 | 43.811 | 44.604 | 45.257 | 45.643 | 45.143 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1446 | 702 | 450 | 340 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 45 | 80.8 | 46.5 | 2 | 470 | CRV 120-5-1C A-D-E-HUBE-E | HUBE
CRV 120-5C | 74125713 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 120.6695 | 115.5757 | 112.4436 | 110.3177 | 107.7322 | 104.6225 | 100.9238 | 96.5716 | 91.5011 | 85.6477 | 35.27 | 41.72 | 43.735 | 44.68 | 45.575 | 46.41 | 47.14 | 47.73 | 48.055 | 47.5 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1476 | 772 | 490 | 370 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 55 | 98.5 | 56.7 | 2 | 575 | CRV 120-5C A-D-E-HUBE-E | HUBE
CRV 120-6-2C | 74125715 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 130.8877 | 127.5236 | 123.4998 | 120.7857 | 117.5568 | 113.7779 | 109.4139 | 104.4298 | 98.7903 | 92.4605 | 35.75 | 44.246 | 46.908 | 48.168 | 49.368 | 50.494 | 51.496 | 52.33 | 52.842 | 52.286 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1628 | 772 | 490 | 370 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 55 | 98.5 | 56.7 | 2 | 585 | CRV 120-6-2C A-D-E-HUBE-E | HUBE
CRV 120-6-1C | 74125714 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 138.713 | 133.882 | 130.083 | 127.5245 | 124.453 | 120.8133 | 116.55 | 111.608 | 105.932 | 99.4667 | 39.037 | 47.155 | 49.695 | 50.892 | 52.029 | 53.093 | 54.032 | 54.803 | 55.254 | 54.643 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1628 | 772 | 490 | 370 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 55 | 98.5 | 56.7 | 2 | 585 | CRV 120-6-1C A-D-E-HUBE-E | HUBE
CRV 120-6C | 74125716 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 143.876 | 138.639 | 134.957 | 132.4496 | 129.4083 | 125.7655 | 121.4539 | 116.4061 | 110.5548 | 103.8325 | 42.324 | 50.064 | 52.482 | 53.616 | 54.69 | 55.692 | 56.568 | 57.276 | 57.666 | 57 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1628 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 705 | CRV 120-6C A-D-E-HUBE-E | HUBE
CRV 120-7-2C | 74125718 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 154.1942 | 150.4508 | 145.8091 | 142.6489 | 138.8689 | 134.424 | 129.2691 | 123.3589 | 116.6486 | 109.0927 | 42.804 | 52.59 | 55.655 | 57.104 | 58.483 | 59.776 | 60.924 | 61.876 | 62.453 | 61.786 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1780 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 715 | CRV 120-7-2C A-D-E-HUBE-E | HUBE
CRV 120-7-1C | 74125717 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160.8924 | 156.1006 | 151.8101 | 148.8752 | 145.3295 | 141.1097 | 136.1525 | 130.3948 | 123.7732 | 116.2244 | 46.091 | 55.499 | 58.442 | 59.828 | 61.144 | 62.375 | 63.46 | 64.349 | 64.865 | 64.143 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1780 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 715 | CRV 120-7-1C A-D-E-HUBE-E | HUBE
CRV 120-7C | 74125719 | 0 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 165.6937 | 162.1763 | 158.3014 | 155.5263 | 152.0947 | 147.9331 | 142.9679 | 137.1256 | 130.3326 | 122.5154 | 49.378 | 58.408 | 61.229 | 62.552 | 63.805 | 64.974 | 65.996 | 66.822 | 67.277 | 66.5 | 2.4 | 2.44 | 2.58 | 2.72 | 2.91 | 3.22 | 3.71 | 4.48 | 5.72 | 8.16 | 0 | 52.61 | 63.52 | 67.53 | 70.57 | 72.68 | 73.84 | 74.07 | 73.38 | 71.75 | 1780 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 715 | CRV 120-7C A-D-E-HUBE-E | HUBE
CRV 150-1-1C | 74126702 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 19.4483 | 18.3 | 17.3985 | 15.9416 | 14.9308 | 13.8879 | 12.7 | 11.4 | 9.9872 | 8.3366 | 4.552 | 6.374 | 6.985 | 7.645 | 7.914 | 8.098 | 8.224 | 8.305 | 8.347 | 8.404 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 834 | 448 | 255 | 182 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 11 | 20.6 | 11.9 | 2 | 230 | CRV 150-1-1C A-D-E-HUBE-E | HUBE
CRV 150-1C | 74126703 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 24.887 | 23.6 | 22.7877 | 21.4193 | 20.4893 | 19.4565 | 18.4 | 17.15 | 15.7 | 14.1 | 7.438 | 10.098 | 10.709 | 11.458 | 11.748 | 11.961 | 12.079 | 12.108 | 12.026 | 11.951 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 834 | 489 | 255 | 182 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 15 | 27.9 | 16 | 2 | 235 | CRV 150-1C A-D-E-HUBE-E | HUBE
CRV 150-2-2C | 74126705 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 40.0385 | 36.2 | 34.5287 | 32.1714 | 30.7683 | 29.2019 | 27.4617 | 25.5373 | 23.4184 | 21.0946 | 9.104 | 12.748 | 13.97 | 15.29 | 15.828 | 16.196 | 16.448 | 16.61 | 16.694 | 16.808 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 986 | 542 | 313 | 257 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 22 | 40.5 | 23.3 | 2 | 250 | CRV 150-2-2C A-D-E-HUBE-E | HUBE
CRV 150-2-1C | 74126704 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 47.4574 | 43.696 | 42.0601 | 39.7858 | 38.3529 | 36.693 | 34.7833 | 32.6015 | 30.125 | 27 | 11.99 | 16.472 | 17.694 | 19.103 | 19.662 | 20.059 | 20.303 | 20.413 | 20.373 | 20.355 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 986 | 580 | 356 | 270 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 22 | 40.5 | 23.3 | 2 | 295 | CRV 150-2-1C A-D-E-HUBE-E | HUBE
CVA 150-2C | 74126706 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 53.9574 | 50.079 | 48.1322 | 45.4669 | 43.8137 | 41.9196 | 39.7639 | 37.3264 | 34.5865 | 31.5237 | 14.876 | 20.196 | 21.418 | 22.916 | 23.496 | 23.922 | 24.158 | 24.216 | 24.052 | 23.902 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 990 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 30 |  |  | 2 | 350 | CRV 150-2C A-D-E-HUBE-E | HUBE
CRV 150-3-2C | 74126708 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 68.4305 | 62.6264 | 59.889 | 56.3006 | 54.1347 | 51.6931 | 48.9546 | 45.8983 | 42.5031 | 38.748 | 16.542 | 22.846 | 24.679 | 26.748 | 27.576 | 28.157 | 28.527 | 28.718 | 28.72 | 28.759 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1142 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 30 | 54.9 | 31.6 | 2 | 360 | CRV 150-3-2C A-D-E-HUBE-E | HUBE
CRV 150-3-1C | 74126707 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 74.9887 | 69.5326 | 67.1128 | 63.7233 | 61.5795 | 59.0907 | 56.2226 | 52.9411 | 49.212 | 45.0011 | 19.428 | 26.57 | 28.403 | 30.561 | 31.41 | 32.02 | 32.382 | 32.521 | 32.399 | 32.306 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1142 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 37 | 67.4 | 38.8 | 2 | 360 | CRV 150-3-1C A-D-E-HUBE-E | HUBE
CRV 150-3C | 74126709 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 83.0381 | 77.7 | 74.8915 | 70.9079 | 68.4591 | 65.6723 | 62.5223 | 58.9843 | 55.0331 | 50.6437 | 22.314 | 30.294 | 32.127 | 34.374 | 35.244 | 35.883 | 36.237 | 36.324 | 36.078 | 35.853 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1142 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 37 | 67.4 | 38.8 | 2 | 385 | CRV 150-3C A-D-E-HUBE-E | HUBE
CRV 150-4-2C | 74126711 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 94.3176 | 88.0266 | 84.6 | 79.8041 | 76.8971 | 73.5901 | 69.8532 | 65.6567 | 60.9708 | 55.7658 | 23.98 | 32.944 | 35.388 | 38.206 | 39.324 | 40.118 | 40.606 | 40.826 | 40.746 | 40.71 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1294 | 702 | 450 | 340 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 45 | 80.8 | 46.5 | 2 | 460 | CRV 150-4-2C A-D-E-HUBE-E | HUBE
CRV 150-4-1C | 74126710 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 104.188 | 95.7055 | 91.9717 | 87.0222 | 84.0023 | 80.5715 | 76.6942 | 72.3345 | 67.457 | 62.0258 | 26.866 | 36.668 | 39.112 | 42.019 | 43.158 | 43.981 | 44.461 | 44.629 | 44.425 | 44.257 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1294 | 702 | 450 | 340 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 45 | 80.8 | 46.5 | 2 | 460 | CRV 150-4-1C A-D-E-HUBE-E | HUBE
CRV 150-4C | 74126712 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 111.9297 | 103.7751 | 100.1 | 94.7124 | 91.5263 | 87.898 | 83.7904 | 79.1666 | 73.9895 | 68.2221 | 29.752 | 40.392 | 42.836 | 45.832 | 46.992 | 47.844 | 48.316 | 48.432 | 48.104 | 47.804 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1324 | 772 | 490 | 370 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 55 | 98.5 | 56.7 | 2 | 560 | CRV 150-4C A-D-E-HUBE-E | HUBE
CRV 150-5-2C | 74126714 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 124.714 | 114.2972 | 109.684 | 103.6163 | 99.9354 | 95.7687 | 91.0758 | 85.8157 | 79.948 | 73.4319 | 31.418 | 43.042 | 46.097 | 49.664 | 51.072 | 52.079 | 52.685 | 52.934 | 52.772 | 52.661 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1476 | 772 | 490 | 370 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 55 | 98.5 | 56.7 | 2 | 690 | CRV 150-5-2C A-D-E-HUBE-E | HUBE
CRV 150-5-1C | 74126713 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 132.7905 | 121.6936 | 117.3329 | 111.4483 | 107.7956 | 103.5952 | 98.7914 | 93.3287 | 87.1516 | 80.2044 | 34.304 | 46.766 | 49.821 | 53.477 | 54.906 | 55.942 | 56.54 | 56.737 | 56.451 | 56.208 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1476 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 690 | CRV 150-5-1C A-D-E-HUBE-E | HUBE
CRV 150-5C | 74126715 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 140.0615 | 129.1991 | 124.9518 | 119.1081 | 115.434 | 111.1764 | 106.2738 | 100.6648 | 94.2878 | 87.0815 | 37.19 | 50.49 | 53.545 | 57.29 | 58.74 | 59.805 | 60.395 | 60.54 | 60.13 | 59.755 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1476 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 690 | CRV 150-5C A-D-E-HUBE-E | HUBE
CRV 150-6-2C | 74126717 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 148.076 | 139 | 133.7 | 126.3525 | 121.9505 | 117.0047 | 111.4841 | 105.3576 | 98.5942 | 91.1627 | 38.856 | 53.14 | 56.806 | 61.122 | 62.82 | 64.04 | 64.764 | 65.042 | 64.798 | 64.612 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1628 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 700 | CRV 150-6-2C A-D-E-HUBE-E | HUBE
CRV 150-6-1C | 74126716 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 157.956 | 147.0371 | 142.1754 | 135.3903 | 131.1093 | 126.1468 | 120.4358 | 113.9094 | 106.5008 | 98.143 | 41.742 | 56.864 | 60.53 | 64.935 | 66.654 | 67.903 | 68.619 | 68.845 | 68.477 | 68.159 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1628 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 700 | CRV 150-6-1C A-D-E-HUBE-E | HUBE
CRV 150-6C | 74126718 | 0 | 80 | 100 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 172.1908 | 159.0237 | 151.0131 | 140.3569 | 133.7776 | 127.6259 | 120.8484 | 112.5 | 104.201 | 94.2239 | 44.628 | 60.588 | 64.254 | 68.748 | 70.488 | 71.766 | 72.474 | 72.648 | 72.156 | 71.706 | 1.83 | 2.044 | 2.144 | 2.324 | 2.595 | 3.048 | 3.717 | 4.682 | 6.106 | 8.395 | 0 | 55.7 | 63.79 | 69.56 | 71.48 | 72.96 | 73.69 | 73.45 | 72.54 | 71.43 | 1628 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 275 | 340 | 380 | 425 | 500 | 180 | 56 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 700 | CRV 150-6C A-D-E-HUBE-E | HUBE
CRV 200-1CBI | 74127702 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 27.5586 | 25.5599 | 24.8811 | 24.0207 | 22.9355 | 21.5795 | 20 | 17.8579 | 15.3869 | 15.3869 | 11.2579 | 13.2096 | 13.7418 | 14.3667 | 15.057 | 15.7619 | 16.4073 | 16.8955 | 17.1055 | 17.1055 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 915 | 542 | 313 | 257 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 18.5 | 34.2 | 19.7 | 2 | 311 | CRV 200-1C BI-D-E-HUBE-E | HUBE
CRV 200-1CAI | 74127701 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 30.8002 | 29.028 | 28.3772 | 27.5704 | 26.574 | 25.3496 | 23.8543 | 22.0406 | 19.9 | 19.9 | 12.8191 | 15.2992 | 15.9311 | 16.6488 | 17.432 | 18.2416 | 19.0198 | 19.6897 | 20.1559 | 20.1559 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 915 | 580 | 356 | 270 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 22 | 40.5 | 23.3 | 2 | 347 | CRV 200-1C AI-D-E-HUBE-E | HUBE
CRV 200-1C | 74127703 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 40.6768 | 38.5811 | 38.0002 | 37.3075 | 36.456 | 35.3875 | 34.0325 | 32.3106 | 30.1302 | 30.1302 | 17.6811 | 21.2896 | 22.334 | 23.4103 | 24.4698 | 25.4559 | 26.304 | 26.9412 | 27.2868 | 27.2868 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 915 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 30 | 54.9 | 31.6 | 2 | 403 | CRV 200-1C A-D-E-HUBE-E | HUBE
CRV 200-2CBI | 74127704 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 56.3611 | 52.7 | 51.3 | 49.4 | 47.1 | 44.2 | 40.9072 | 36.9334 | 31.8768 | 31.8768 | 22.5158 | 26.4193 | 27.4836 | 28.7334 | 30.114 | 31.5239 | 32.8147 | 33.791 | 34.2109 | 34.2109 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1109 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 37 | 67.4 | 38.8 | 2 | 447 | CRV 200-2C BI-D-E-HUBE-E | HUBE
CRV 200-2CAI | 74127705 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 63.2053 | 59.386 | 57.9558 | 56.2712 | 54.2561 | 51.8033 | 48.7744 | 45.0002 | 40.2801 | 40.2801 | 25.6381 | 30.5984 | 31.8622 | 33.2976 | 34.864 | 36.4833 | 38.0396 | 39.3794 | 40.3118 | 40.3118 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1139 | 702 | 450 | 340 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 45 | 80.8 | 46.5 | 2 | 504 | CRV 200-2C AI-D-E-HUBE-E | HUBE
CRV 200-2-1CAI | 74127706 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 72.9576 | 69.1272 | 67.7678 | 66.1588 | 64.2273 | 61.8751 | 58.9786 | 55.3889 | 50.9316 | 50.9316 | 30.5002 | 36.5888 | 38.2651 | 40.059 | 41.9018 | 43.6975 | 45.3238 | 46.6309 | 47.4427 | 47.4427 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1139 | 772 | 490 | 370 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 55 | 98.5 | 56.7 | 2 | 595 | CRV 200-2-1C AI-D-E-HUBE-E | HUBE
CRV 200-2C | 74127707 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 82.7557 | 78.6445 | 77.3626 | 75.8449 | 74.0199 | 71.7979 | 69.0715 | 65.7148 | 61.5843 | 61.5843 | 35.3622 | 42.5792 | 44.668 | 46.8205 | 48.9395 | 50.9118 | 52.608 | 53.8824 | 54.5736 | 54.5736 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1139 | 772 | 490 | 370 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 55 | 98.5 | 56.7 | 2 | 595 | CRV 200-2C A-D-E-HUBE-E | HUBE
CRV 200-3-2CBI | 74127709 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 97.1977 | 91.5156 | 89.1076 | 86.3573 | 83.192 | 79.4853 | 75.0572 | 69.6738 | 63.0474 | 63.0474 | 40.1969 | 47.7089 | 49.8176 | 52.1436 | 54.5838 | 56.9798 | 59.1186 | 60.7323 | 61.4977 | 61.4977 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1333 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 748 | CRV 200-3-2C BI-D-E-HUBE-E | HUBE
CRV 200-3-2CABI | 74127708 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 101.3595 | 95.0727 | 92.8045 | 90.1734 | 87.0907 | 83.429 | 79.0219 | 73.6645 | 67.1128 | 67.1128 | 41.7581 | 49.7985 | 52.0069 | 54.4257 | 56.9588 | 59.4595 | 61.7311 | 63.5265 | 64.5482 | 64.5482 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1333 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 748 | CRV 200-3-2C ABI-D-E-HUBE-E | HUBE
CRV 200-3-2CAI | 74127710 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 105.7619 | 99.5193 | 97.2721 | 94.7396 | 91.8155 | 88.3301 | 84.0504 | 78.6798 | 71.8588 | 71.8588 | 43.3192 | 51.888 | 54.1962 | 56.7078 | 59.3338 | 61.9392 | 64.3435 | 66.3207 | 67.5986 | 67.5986 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1333 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 748 | CRV 200-3-2C AI-D-E-HUBE-E | HUBE
CRV 200-3-1CBI | 74127711 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 110.675 | 104.6422 | 102.3852 | 99.8197 | 96.8585 | 93.3617 | 89.1367 | 83.9384 | 77.4691 | 77.4691 | 46.6201 | 55.7889 | 58.4098 | 61.1872 | 63.9965 | 66.6738 | 69.0153 | 70.778 | 71.6791 | 71.6791 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1333 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 748 | CRV 200-3-1C BI-D-E-HUBE-E | HUBE
CRV 200-3-1CAI | 74127712 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 113.8397 | 108.0372 | 105.9334 | 103.5207 | 100.7016 | 97.3287 | 93.2045 | 88.082 | 81.6639 | 81.6639 | 48.1813 | 57.8784 | 60.5991 | 63.4693 | 66.3715 | 69.1534 | 71.6277 | 73.5722 | 74.7295 | 74.7295 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1333 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | 748 | CRV 200-3-1C AI-D-E-HUBE-E | HUBE
CRV 200-3C | 74127713 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 123.6323 | 117.7677 | 115.6674 | 113.2866 | 110.5294 | 107.2454 | 103.2305 | 98.2262 | 91.9199 | 91.9199 | 53.0433 | 63.8689 | 67.002 | 70.2308 | 73.4093 | 76.3677 | 78.912 | 80.8237 | 81.8604 | 81.8604 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1333 | 890 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 90 | 159.9 | 92.1 | 2 | 817 | CRV 200-3C A-D-E-HUBE-E | HUBE
CRV 200-4-2CBI | 74127714 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 139.9917 | 131.7725 | 128.7256 | 125.1703 | 120.9898 | 116.0182 | 110.0396 | 102.7889 | 93.9514 | 93.9514 | 57.878 | 68.9985 | 72.1516 | 75.5539 | 79.0535 | 82.4357 | 85.4226 | 87.6735 | 88.7845 | 88.7845 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1527 | 890 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 90 | 159.9 | 92.1 | 2 | 830 | CRV 200-4-2C BI-D-E-HUBE-E | HUBE
CRV 200-4-2CAI | 74127715 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 146.599 | 138.6356 | 135.6293 | 132.218 | 128.2859 | 123.6447 | 118.034 | 111.1214 | 102.5021 | 102.5021 | 61.0003 | 73.1777 | 76.5302 | 80.1181 | 83.8035 | 87.3951 | 90.6475 | 93.2619 | 94.8854 | 94.8854 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1527 | 1140 | 645 | 540 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 110 | 195.1 | 112.3 | 2 | 1180 | CRV 200-4-2C AI-D-E-HUBE-E | HUBE
CRV 200-4-1CAI | 74127716 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 156.3952 | 148.1639 | 145.3743 | 142.164 | 138.3998 | 133.8909 | 128.3882 | 121.5849 | 113.116 | 113.116 | 65.8624 | 79.1681 | 82.9331 | 86.8795 | 90.8413 | 94.6094 | 97.9317 | 100.5134 | 102.0163 | 102.0163 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1527 | 1140 | 645 | 540 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 110 | 195.1 | 112.3 | 2 | 1180 | CRV 200-4-1C AI-D-E-HUBE-E | HUBE
CRV 200-4C | 74127717 | 0 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 240 | 165.8701 | 157.8333 | 155.1704 | 152.0298 | 148.2858 | 143.7773 | 138.3076 | 131.644 | 123.5182 | 123.5182 | 70.7244 | 85.1585 | 89.336 | 93.641 | 97.8791 | 101.8236 | 105.2159 | 107.7649 | 109.1472 | 109.1472 | 2.26 | 2.42 | 2.52 | 2.657 | 2.832 | 3.126 | 3.645 | 4.57 | 6.492 | 6.492 | 0 | 52.4 | 60.06 | 66.63 | 71.33 | 74.45 | 76.66 | 77.9 | 78.6 | 78.6 | 1527 | 1140 | 645 | 540 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 110 | 195.1 | 112.3 | 2 | 1180 | CRV 200-4C A-D-E-HUBE-E | HUBE
CRV 320-1-1C | При заказе | 0 | 200 | 240 | 260 | 280 | 300 | 320 | 340 | 360 | 360 | 36.8 | 30.3 | 27.8 | 25.85 | 23.7 | 21.18 | 18.17 | 14 | 6.4 | 6.4 | 9.433 | 21.974 | 23.5 | 24.142 | 24.704 | 25.186 | 25.588 | 25.911 | 26.153 | 26.153 | 2.34 | 2.5 | 2.621 | 2.779 | 3.076 | 3.581 | 4.404 | 5.755 | 8.205 | 8.205 | 0 | 61.29 | 67.29 | 69.19 | 70.7 | 71.81 | 72.53 | 72.86 | 72.79 | 72.79 | 915 | 653 | 395 | 304 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 30 | 54.9 | 31.6 | 2 | По запросу | CRV 320-1-1C A-D-E-HUBE-E | HUBE
CRV 320-1C | При заказе | 0 | 200 | 240 | 260 | 280 | 300 | 320 | 340 | 360 | 360 | 46.38 | 38.5 | 35.2 | 33.05 | 30.38 | 27.52 | 24.04 | 19.1 | 10.42 | 10.42 | 18.236 | 34.616 | 36.907 | 37.934 | 38.883 | 39.754 | 40.547 | 41.263 | 41.9 | 41.9 | 2.34 | 2.5 | 2.621 | 2.779 | 3.076 | 3.581 | 4.404 | 5.755 | 8.205 | 8.205 | 0 | 61.29 | 67.29 | 69.19 | 70.7 | 71.81 | 72.53 | 72.86 | 72.79 | 72.79 | 945 | 702 | 450 | 340 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 45 | 80.8 | 46.5 | 2 | По запросу | CRV 320-1C A-D-E-HUBE-E | HUBE
CRV 320-2-2C | При заказе | 0 | 200 | 240 | 260 | 280 | 300 | 320 | 340 | 360 | 360 | 73.88 | 61.3 | 56 | 51.99 | 47.8 | 42.84 | 36.75 | 28.5 | 13.51 | 13.51 | 18.866 | 43.948 | 47 | 48.284 | 49.408 | 50.372 | 51.176 | 51.822 | 52.306 | 52.306 | 2.34 | 2.5 | 2.621 | 2.779 | 3.076 | 3.581 | 4.404 | 5.755 | 8.205 | 8.205 | 0 | 61.29 | 67.29 | 69.19 | 70.7 | 71.81 | 72.53 | 72.86 | 72.79 | 72.79 | 1139 | 772 | 490 | 370 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 55 | 98.5 | 56.7 | 2 | По запросу | CRV 320-2-2C A-D-E-HUBE-E | HUBE
CRV 320-2-1C | При заказе | 0 | 200 | 240 | 260 | 280 | 300 | 320 | 340 | 360 | 360 | 82.8 | 69 | 63.2 | 58.74 | 54.18 | 48.81 | 42.27 | 33.2 | 17.29 | 17.29 | 27.669 | 56.59 | 60.407 | 62.076 | 63.587 | 64.94 | 66.135 | 67.174 | 68.053 | 68.053 | 2.34 | 2.5 | 2.621 | 2.779 | 3.076 | 3.581 | 4.404 | 5.755 | 8.205 | 8.205 | 0 | 61.29 | 67.29 | 69.19 | 70.7 | 71.81 | 72.53 | 72.86 | 72.79 | 72.79 | 1139 | 840 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 75 | 133.7 | 77 | 2 | По запросу | CRV 320-2-1C A-D-E-HUBE-E | HUBE
CRV 320-2C | При заказе | 0 | 200 | 240 | 260 | 280 | 300 | 320 | 340 | 360 | 360 | 92.94 | 77.6 | 70.7 | 65.9 | 60.85 | 54.97 | 47.92 | 38.5 | 21.82 | 21.82 | 36.472 | 69.232 | 73.814 | 75.868 | 77.766 | 79.508 | 81.094 | 82.526 | 83.8 | 83.8 | 2.34 | 2.5 | 2.621 | 2.779 | 3.076 | 3.581 | 4.404 | 5.755 | 8.205 | 8.205 | 0 | 61.29 | 67.29 | 69.19 | 70.7 | 71.81 | 72.53 | 72.86 | 72.79 | 72.79 | 1139 | 890 | 550 | 410 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 90 | 159.9 | 92.1 | 2 | По запросу | CRV 320-2C A-D-E-HUBE-E | HUBE
CRV 320-3-2C | При заказе | 0 | 200 | 240 | 260 | 280 | 300 | 320 | 340 | 360 | 360 | 119.93 | 100.7 | 91.7 | 85.18 | 78.45 | 70.63 | 61.21 | 48.4 | 24.29 | 24.29 | 37.102 | 78.564 | 83.907 | 86.218 | 88.291 | 90.126 | 91.723 | 93.085 | 94.206 | 94.206 | 2.34 | 2.5 | 2.621 | 2.779 | 3.076 | 3.581 | 4.404 | 5.755 | 8.205 | 8.205 | 0 | 61.29 | 67.29 | 69.19 | 70.7 | 71.81 | 72.53 | 72.86 | 72.79 | 72.79 | 1333 | 1140 | 645 | 540 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 110 | 195.1 | 112.3 | 2 | По запросу | CRV 320-3-2C A-D-E-HUBE-E | HUBE
CRV 320-3-1C | При заказе | 0 | 200 | 240 | 260 | 280 | 300 | 320 | 340 | 360 | 360 | 129.76 | 108.32 | 98.5 | 91.83 | 84.86 | 76.8 | 67.14 | 54.2 | 29.72 | 29.72 | 45.905 | 91.206 | 97.314 | 100.01 | 102.47 | 104.694 | 106.682 | 108.437 | 109.953 | 109.953 | 2.34 | 2.5 | 2.621 | 2.779 | 3.076 | 3.581 | 4.404 | 5.755 | 8.205 | 8.205 | 0 | 61.29 | 67.29 | 69.19 | 70.7 | 71.81 | 72.53 | 72.86 | 72.79 | 72.79 | 1333 | 1140 | 645 | 540 | Ø150 | Ø250 | Ø298 | Ø203 | 385 | 460 | 490 | 500 | 610 | 200 | 60 | 8xØ28 | 4xØ23 | 25 | DN 150 | DN 150 | 110 | 195.1 | 112.3 | 2 | По запросу | CRV 320-3-1C A-D-E-HUBE-E | HUBE

## NBV
Насос | Артикул | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | Q9 | Q10 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8 | H9 | H10 | P1 | P2 | P3 | P4 | P5 | P6 | P7 | P8 | P9 | P10 | NPSH1 | NPSH2 | NPSH3 | NPSH4 | NPSH5 | NPSH6 | NPSH7 | NPSH8 | NPSH9 | NPSH10 | КПД1 | КПД2 | КПД3 | КПД4 | КПД5 | КПД6 | КПД7 | КПД8 | КПД9 | КПД10 | B1 | B2 | D1 | D2 | D3 | D4 | D5 | D6 | a1 | a2 | a3 | a4 | a5 | Hh1 | Hh2 | nxd1 | nxd2 | Давл, бар | Вход | Выход | P2, кВт | I, А △ | I, А Y | pole | Вес (Нетто), кг | Наименование | Торцевое
CRV 1-2C | 74111740 | 0 | 0.8 | 1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.4 | 12.3244 | 11.5222 | 11.2219 | 10.8476 | 10.3913 | 9.8504 | 9.2276 | 8.5311 | 7.774 | 6.85 | 0.0424 | 0.0726 | 0.0782 | 0.083 | 0.0868 | 0.0896 | 0.0914 | 0.0924 | 0.0926 | 0.0916 | 1.024 | 1.035 | 1.033 | 1.059 | 1.115 | 1.212 | 1.368 | 1.611 | 1.905 | 2.313 | 0 | 34.2 | 40.49 | 44.19 | 46.64 | 47.81 | 47.59 | 45.83 | 42.26 | 36.55 | 254 | 207 | 134 | 112 | ø32 | ø89 | ø140 | ø100 | 100 | 150 | 250 | 180 | 210 | 75 | 30 | 4х19х24,5 | 4хø13 | 25 | DN 25/32 | DN 25/32 | 0.37 | 1.6 | 0.9 | 2 | 21 | CRV 1-2C A-D-E-HQQE-E | HQQE

## motors
| P2, кВт | Freq, Гц | U, В | I, А △ | I, А Y | Cos φ | n, об/мин | cpa, % | IE
CRV | 0.37 | 50 | 3 x 220D/380Y | 1.6 | 0.9 | 0.81 | 2930 | 73.8 | 3
CRV | 0.55 | 50 | 3 x 220D/380Y | 2.3 | 1.3 | 0.82 | 2930 | 77.8 | 3
CRV | 0.75 | 50 | 3 x 220D/380Y | 3 | 1.7 | 0.82 | 2930 | 80.7 | 3
CRV | 1.1 | 50 | 3 x 220D/380Y | 4.2 | 2.4 | 0.83 | 2945 | 82.7 | 3
CRV | 1.5 | 50 | 3 x 220D/380Y | 5.6 | 3.2 | 0.84 | 2940 | 84.2 | 3
CRV | 2.2 | 50 | 3 x 220D/380Y | 7.9 | 4.6 | 0.85 | 2955 | 85.9 | 3
CRV | 3 | 50 | 3 x 220D/380Y | 10.4 | 6 | 0.87 | 2960 | 87.1 | 3
CRV | 4 | 50 | 3 x 380D/660Y | 7.8 | 4.5 | 0.88 | 2960 | 88.1 | 3
CRV | 5.5 | 50 | 3 x 380D/660Y | 10.6 | 6.1 | 0.88 | 2930 | 89.2 | 3
CRV | 7.5 | 50 | 3 x 380D/660Y | 14.4 | 8.3 | 0.88 | 2930 | 90.1 | 3
CRV | 11 | 50 | 3 x 380D/660Y | 20.6 | 11.9 | 0.89 | 2930 | 91.2 | 3
CRV | 15 | 50 | 3 x 380D/660Y | 27.9 | 16 | 0.89 | 2945 | 91.9 | 3
CRV | 18.5 | 50 | 3 x 380D/660Y | 34.2 | 19.7 | 0.89 | 2940 | 92.4 | 3
CRV | 22 | 50 | 3 x 380D/660Y | 40.5 | 23.3 | 0.89 | 2955 | 92.7 | 3
CRV | 30 | 50 | 3 x 380D/660Y | 54.9 | 31.6 | 0.89 | 2960 | 93.3 | 3
CRV | 37 | 50 | 3 x 380D/660Y | 67.4 | 38.8 | 0.89 | 2960 | 93.7 | 3
CRV | 45 | 50 | 3 x 380D/660Y | 80.8 | 46.5 | 0.9 | 2965 | 94 | 3
CRV | 55 | 50 | 3 x 380D/660Y | 98.5 | 56.7 | 0.9 | 2970 | 94.3 | 3
CRV | 75 | 50 | 3 x 380D/660Y | 133.7 | 77 | 0.9 | 2970 | 94.7 | 3
CRV | 90 | 50 | 3 x 380D/660Y | 159.9 | 92.1 | 0.9 | 2970 | 95 | 3
CRV | 110 | 50 | 3 x 380D/660Y | 195.1 | 112.3 | 0.9 | 2970 | 95.2 | 3

## DO NOT DELETE - AutoCrat Job Se (hidden)
Job ID | Job Name | Template ID | Data Sheet ID | Header Row | First Data Row | File Name | File Type | Share As | Folders | Dynamic Folder Reference | Conditionals | Mode | Append Breaks | Tags | Run On Time Trigger | Time Trigger Frequency | Run On Form Trigger | Send Email And Share | Email To | Email CC | Email BCC | Email Reply To | Email No Reply | Email Subject | Email Body | Prevent Resharing | Time Trigger Timestamp | Form Trigger Timestamp